## TC-C.B-Fuse
Enter Data in White Background Cells
Calculate Size of Transformer / Fuse / Circuit Breaker | [7 empty] | Jignesh.Parmar www.electricalnotes.wordpress.com, jiguparmar@yahoo.com
Calculation Size of Circuit Breaker & Fuse are as per NEC 450.3
CONNECTED EQUIPMENT TO TRANSFORMER | [7 empty] | Transformer Details
Sr.No | Equipment | Kw | P.F | Qty | Equipment D.F | Total Kva | D.F (Kva) | Total D.F Load | 3 | Kva | [5 empty] | Y-Y | 1
|  | 3 | 1 | 1 | 100% | 3 | 3 | Primary Side Voltage (L-L): | 415 | Volt |  |  | 0 |  |  | ∆-∆ |  | Primary Only
[6 empty] | 0 | 0 | Secondary Side Voltage (L-L): | 230 | Volt |  |  | 0 |  |  | Y-∆ |  | Pri.Side & Sec.Side
[6 empty] | 0 | 0 | Transformer Impedance: | 5% |  |  |  | 1 |  |  | ∆-Y
[6 empty] | 0 | 0 | Transformer Connection | Y-Y |  |  |  | TRUE
[6 empty] | 0 | 0 | Size of Transformer: | 3 | Kva OR | Kva | 3 | TRUE
[6 empty] | 0 | 0 | Efficency of Transformer at Full Load | 98.4% | 0.984
[6 empty] | 0 | 0 | Efficency of Transformer at 1/4 Load | 97.5% | 0.975
[6 empty] | 0 | 0 | Location of Transformer
[6 empty] | 0 | 0 | Provide Protection on Transformer: | Primary Only
[6 empty] | 0 | 0 | Type Protection on Primary & Secondary Side: | [6 empty] | 1 | 2 | 3 | 4
[6 empty] | 0 | 0 | :Results: | [6 empty] | 1 | 2 | 3 | 4
[6 empty] | 0 | 0 | Transformer Voltage / Current | [6 empty] | Y-Y | D-D | Y-D | D-Y
[6 empty] | 0 | 0 | Primary Line Voltage (L-L) | 415 | Volt |  |  |  | 415 | 415 | 415 | 415 | 415
[6 empty] | 0 | 0 | Primary Phase Voltage (L-P) | 239.6074 | Volt |  |  |  | 239.6074 | 239.6074 | 415 | 239.6074 | 415
[6 empty] | 0 | 0 | Primary Line Current(L-L): | 4.1737 | Amp |  |  |  | 4.1737 | 4.1737 | 4.1737 | 4.1737 | 4.1737
[6 empty] | 0 | 0 | Primary Phase Current(L-P): | 4.1737 | Amp |  |  |  | 4.1737 | 4.1737 | 2.4098 | 4.1737 | 2.4098
[6 empty] | 0 | 0 | Secondary Line Voltage (L-L) | 230 | Volt |  |  |  | 230 | 230 | 230 | 230 | 230
[6 empty] | 0 | 0 | Secondary Phase Voltage (L-P) | 132.7945 | Volt |  |  |  | 132.7945 | 132.7945 | 230 | 230 | 132.7945
[6 empty] | 0 | 0 | Secondary Phase Current(L-P): | 7.5309 | Amp |  |  |  | 7.5309 | 7.5309 | 7.5309 | 7.5309 | 7.5309
[6 empty] | 0 | 0 | Secondary Line Current(L-L): | 7.5309 | Amp |  |  |  | 7.5309 | 7.5309 | 4.3481 | 4.3481 | 7.5309
[6 empty] | 0 | 0 | Size of Circuit Breaker / Fuse (As per NEC 450.3)
[6 empty] | 0 | 0 | Size of Circuit Breaker on Primary Side: | 6 | Amp
[6 empty] | 0 | 0 | Size of Fuse on Primary Side: | 6 | Amp
[6 empty] | 0 | 0 | Size of Circuit Breaker on Secondary Side: | N/A | Amp
[6 empty] | 0 | 0 | Size of Fuse on Secondary Side: | N/A | Amp
[6 empty] | 0 | 0 | Transformer Losses
[6 empty] | 0 | 0 | Total Losses@ Full Load | 48.7805 | Watt
[6 empty] | 0 | 0 | Total Losses@ 1/4 Load | 19.2308 | Watt
[5 empty] | Total Load (Kva) |  | 3 | Full Load Copper Loss | 31.5197 | Watt
[5 empty] | Total Load D.F |  | 100% | Core Loss | 17.2608 | Watt
[5 empty] | Total D.F (Kva) |  | 3
Enter Detail of TC/CB/Fuse
Supervised
Not Supervised
Circuit Breaker
Fuse

## Sheet2
Size of Transformer / Fuse / Circuit Breaker | [6 empty] | 2
[6 empty] | 3 | 3
|  | UnSupervised |  | Supervised |  | 2 | 3 | 6
Standard Size of 3 Phase Transformer (KVA) | Standard Size of Fuse / C.B (Amp) | Fuse / Inverse Time C.B as per NEC (Amp) |  | Fuse / Inverse Time C.B as per NEC (Amp) |  | 3 Phase T.C (KVA) |  |  | 1 | Primary |  | Secondary |  |  | 0
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 |  | C.B | Fuse | C.B | Fuse
3 | 3 | 3 | 6 | 3 | 3 | 3 | 3 | 6 | 1 | 600% | 300% | 250% | 250%
6 | 6 | 6 | 10 | 6 | 6 | 6 | 6 | 9 | 2 | 600% | 300% | 125% | 125%
9 | 10 | 10 | 15 | 10 | 10 | 9 | 9 | 15 |  | 600% | 300% | 250% | 250% |  | Primary |  | Secondary
15 | 15 | 15 | 20 | 15 | 15 | 15 | 15 | 25 |  | 25.0424 | 12.5212 | 18.8272 | 18.8272 |  | C.B | Fuse | C.B | Fuse
25 | 20 | 20 | 25 | 20 | 20 | 25 | 25 | 30 |  | 25 | 10 | 15 | 15 |  | 6 | 6 | N/A | N/A
30 | 25 | 25 | 30 | 25 | 25 | 30 | 30 | 37.5
37.5 | 30 | 30 | 35 | 30 | 30 | 37.5 | 37.5 | 45
45 | 35 | 35 | 40 | 35 | 35 | 45 | 45 | 50
50 | 40 | 40 | 45 | 40 | 40 | 50 | 50 | 75 |  | More Than 600V |  |  |  | Supervised
75 | 45 | 45 | 50 | 45 | 45 | 75 | 75 | 112.5 |  | %Imp | Primary |  | secondary
112.5 | 50 | 50 | 60 | 50 | 50 | 112.5 | 112.5 | 150 |  |  | >600 |  | >600 |  | <600
150 | 60 | 60 | 70 | 60 | 60 | 150 | 150 | 225 |  |  | C.B | Fuse | C.B | Fuse | C.B/Fuse
225 | 70 | 70 | 80 | 70 | 70 | 225 | 225 | 300
300 | 80 | 80 | 90 | 80 | 80 | 300 | 300 | 500 |  | 1% | 600% | 300% | 300% | 250% | 250%
500 | 90 | 90 | 100 | 90 | 90 | 500 | 500 | 750 |  | 2% | 600% | 300% | 300% | 250% | 250%
750 | 100 | 100 | 110 | 100 | 100 | 750 | 750 | 1000 |  | 3% | 600% | 300% | 300% | 250% | 250%
1000 | 110 | 110 | 125 | 110 | 110 | 1000 | 1000 | 1500 |  | 4% | 600% | 300% | 300% | 250% | 250%
1500 | 125 | 125 | 150 | 125 | 125 | 1500 | 1500 | 2000 |  | 5% | 600% | 300% | 300% | 250% | 250%
2000 | 150 | 150 | 160 | 150 | 150 | 2000 | 2000 | 2500 |  | 6% | 600% | 300% | 300% | 250% | 250%
2500 | 160 | 160 | 175 | 160 | 160 | 2500 | 2500 | 3750 |  | 7% | 400% | 300% | 250% | 225% | 250%
3750 | 175 | 175 | 200 | 175 | 175 | 3750 | 3750 | 5000 |  | 8% | 400% | 300% | 250% | 225% | 250%
5000 | 200 | 200 | 225 | 200 | 200 | 5000 | 5000 | 7500 |  | 9% | 400% | 300% | 250% | 225% | 250%
7500 | 225 | 225 | 250 | 225 | 225 | 7500 | 7500 | 10000 |  | 10% | 400% | 300% | 250% | 225% | 250%
10000 | 250 | 250 | 300 | 250 | 250 | 10000 | 10000 | 12000
12000 | 300 | 300 | 350 | 300 | 300 | 12000 | 12000 | 15000
15000 | 350 | 350 | 400 | 350 | 350 | 15000 | 15000 | 20000
20000 | 400 | 400 | 450 | 400 | 400 | 20000 | 20000 | 25000 | Prim. | 5% | 0 | C.B | 600% | Fuse | 300%
25000 | 450 | 450 | 500 | 450 | 450 | 25000 | 25000 | 30000 | Sec. |  | 0 | C.B | 250% | Fuse | 250%
30000 | 500 | 500 | 600 | 500 | 500 | 30000 | 30000 | 37500
37500 | 600 | 600 | 700 | 600 | 600 | 37500 | 37500 | 50000
50000 | 700 | 700 | 800 | 700 | 700 | 50000 | 50000 | 60000
60000 | 800 | 800 | 1000 | 800 | 800 | 60000 | 60000 | 75000
75000 | 1000 | 1000 | 1200 | 1000 | 1000 | 75000 | 75000 | 100000 | Prim. | 5% | 0 | C.B | 600% | Fuse | 300%
100000 | 1200 | 1200 | 1600 | 1200 | 1200 | 100000 | 100000 | 100000 | Sec. |  | 0 | C.B | 125% | Fuse | 125%
| 1600 | 1600 | 2000 | 1600 | 1600
| 2000 | 2000 | 2500 | 2000 | 2000
| 2500 | 2500 | 3000 | 2500 | 2500
| 3000 | 3000 | 4000 | 3000 | 3000
| 4000 | 4000 | 5000 | 4000 | 4000
| 5000 | 5000 | 6000 | 5000 | 5000
| 6000 | 6000 | 6000 | 6000 | 6000
[10 empty] | More Than 600V |  |  |  | Not Supervised
[10 empty] | %Imp | Primary |  | secondary
[11 empty] | >600 |  | >600 |  | <600
[11 empty] | C.B | Fuse | C.B | Fuse | C.B/Fuse
[10 empty] | 1% | 600% | 300% | 300% | 250% | 125%
[10 empty] | 2% | 600% | 300% | 300% | 250% | 125%
[10 empty] | 3% | 600% | 300% | 300% | 250% | 125%
[10 empty] | 4% | 600% | 300% | 300% | 250% | 125%
[10 empty] | 5% | 600% | 300% | 300% | 250% | 125%
[10 empty] | 6% | 600% | 300% | 300% | 250% | 125%
[10 empty] | 7% | 400% | 300% | 250% | 225% | 125%
[10 empty] | 8% | 400% | 300% | 250% | 225% | 125%
[10 empty] | 9% | 400% | 300% | 250% | 225% | 125%
[10 empty] | 10% | 400% | 300% | 250% | 225% | 125%
Maximum Rating of Over current Protection for Transformers Less than 600 Volts
[10 empty] | Protection | Primary Protection |  |  | Secondary Protection
[10 empty] | Method | More than 9A | 2A to 9A | Less than 2A | More than 9A | Less than 9A
[10 empty] | Primary only protection | 125%(NH) | 167% | 300% | Not required | Not required
[10 empty] | Primary and secondary protection | 250% | 250% | 250% | 125%(NH) | 167%
[9 empty] | Primary Only | Primary only protection
[10 empty] | Amp | Pri | Sec
[10 empty] | 1 | 300% | 0%
[10 empty] | 2 | 167% | 0%
[10 empty] | 3 | 167% | 0%
[10 empty] | 4 | 167% | 0%
[10 empty] | 5 | 167% | 0%
[10 empty] | 6 | 167% | 0%
[10 empty] | 7 | 167% | 0%
[10 empty] | 8 | 167% | 0%
[10 empty] | 9 | 167% | 0%
[10 empty] | 10 | 125% | 0%
[9 empty] | 4.1737 |  | 167% | 0% | 0
[9 empty] | 7.5309 |  | 6.9701 | N/A
[11 empty] | 6 | N/A
Primary & Secondary protection
[10 empty] | Amp | Pri | Sec
[10 empty] | 1 | 250% | 167%
[10 empty] | 2 | 250% | 167%
[10 empty] | 3 | 250% | 167%
[10 empty] | 4 | 250% | 167%
[10 empty] | 5 | 250% | 167%
[10 empty] | 6 | 250% | 167%
[10 empty] | 7 | 250% | 167%
[10 empty] | 8 | 250% | 167%
[10 empty] | 9 | 250% | 125%
[10 empty] | 10 | 250% | 125%
[9 empty] | 4.1737 |  | 250% | 167% | 0
[9 empty] | 7.5309 |  | 10.4343 | 12.5766
[11 empty] | 10 | 10
[11 empty] | 6 | N/A
HOME