Energy Infrastructure for AI Data Centers: A Critical Review of Grid Integration, Techno-Economic Challenges, and Future Pathways

Mahmoud Kiasari, Hamed Aly

Smart grid and Green Power Research Lab, Electrical and Computer Engineering Department, Faculty of Engineering, Dalhousie University, Halifax, Nova Scotia, Canada

Mahmoud.Kiasari@dal.ca, Hamed.Aly@dal.ca

Abstract: The intense growth of artificial intelligence (AI) workloads is driving global data center electricity demand to hit a projected 945 TWh by 2030, up from approximately 415 TWh today. The critical challenge lies in satisfying this exponential growth while simultaneously meeting climate goals and ensuring economic sustainability.

To address this, this study introduces a seven-component design framework covering the technical, economic, and regulatory dimensions of sustainable computing infrastructure. The framework integrates site assessment, technology selection, electrical architecture design, hierarchical control, demand-side workload flexibility, economic viability analysis, and regulatory compliance.

Synthesized from a comprehensive review of over 185 peer-reviewed articles, industry reports, and policy documents, this study combines current knowledge in renewable technologies, energy storage, power system modeling, and operations. This framework is validated by global tech case studies achieving cost-competitive electricity delivery at $35–$100/MWh alongside >99.9% reliability targets.

Key findings indicate that lithium-ion battery prices are projected to fall below $108/kWh in 2026, solar PV installation costs have dropped over 90% since 2010, and geographic diversification leveraging wind-solar complementarity can reduce required storage capacity by 40% to 60%. Detailed economic modeling, including levelized cost of energy (LCOE), net present value (NPV), and sensitivity assessments demonstrates viable payback periods of 5–12 years under current tax incentives. Finally, a multi-year implementation roadmap spanning 2024–2045 outlines the phased transition pathway from localized, demonstration-scale projects to mainstream, 100% renewable-powered AI data center infrastructure.

Keywords: AI data centers, renewable energy integration, energy storage, microgrid optimization, power system modelling, demand-side management, carbon-free energy, levelized cost of energy

1. Introduction

1.1. Global Data Center Energy Consumption and AI workload Growth

In the last ten years, the entire digital infrastructure has been revolutionized, and the main driver behind this is the explosion of applications based on Artificial Intelligence. Data canters alone are a huge component of this infrastructure and are expected to use approximately 415 TWh of electricity in 2024, which is approximately 1.5% of the world[1], [2]. According to the International Energy Agency (IEA), this consumption may grow to 945 TWh by 2030 based on current growth rates, mainly because of the training and inferring workloads of AI models[3]. This is a staggering leap, feeding the electricity use of a power-hungry country the size of Japan into the global grid in just six years, and shows how critical it is to move towards sustainable energy solutions in data center operations.

This challenge is evident in the energy consumption of specific AI models. To train GPT-3, a 175-billion-parameter language model developed by OpenAI, approximately 1, 287 MWh of electricity was required, which corresponds to an estimated CO2 equivalent emission of 552 tones[4], [5]. The next GPT, with significantly more parameters, would have an even greater energy cost. Exact numbers are still proprietary, but such a model would likely be even more costly on a per-use basis. The model called BLOOM [6] is an open-source model consisting of 176 billion parameters that took approximately 433 MWh in training. These are the numbers of single training events; the total amount of energy used by constant inferences per year to serve billions of user queries is much higher than the training energy. According to research by Li, every inference query of GPT-3 consumes around 2.9 Wh of electricity and adds up to a massive amount with the millions of queries that take place every year[7].

One of the biggest tipping points in electricity demand growth since the electrification of industry will come with AI, with one research group estimating [8] that power demand in data centers would grow at a rate of 165% by 2030. However, the Power Usage Effectiveness (PUE) of the surveyed locations did not show any significant gains in efficiency as measured by PUE, according to the Uptime Institute 2024 Global Data Center Survey[9]. Meanwhile, AI-specific accelerators, such as the NVIDIA H100 GPU, with a thermal design power (TDP) of up to 700 watts per unit, are pushing the compute density to levels that challenge conventional cooling and power delivery architectures[10]. Fig. 1 illustrates this growth trajectory, showing historical data center electricity consumption from 2015 to 2024 alongside IEA projections to 2030, with the AI-driven inflection point clearly visible after 2022.

Figure 1: Global data center electricity consumption and projections (2015–2030). Source: IEA, 2025

1.2. The Renewable Energy Imperative

Three simultaneous drivers, namely, climate goals, cost trends, and growing technical viability, are coming together in data center power systems for the integration of renewable energy sources. With over 130 countries aligning themselves to reach zero carbon emissions by 2050 under the Paris Agreement, the information technology sector has emerged as a critical focus area for decarbonization efforts[11]. Major technology firms such as Google, Microsoft, and Meta have all committed to running 24/7 carbon-free energy (CFE) operations by 2030, a criterion that includes matching all hours of electricity use with clean generation, not accounting for it on an annual basis using renewable electricity certificates (RECs)[12].

The price curve of renewable energy technologies has reshaped the way data centers purchase power. PV module prices have dropped by more than 90% since 2010, to approximately $0.15 to $0.25 per watt for commercial-grade modules in 2024, and PV system costs for ground-mounted utility-scale systems are approximately $0.75 to $1.40 per watt[13], [14]. Onshore wind has also performed well, with capacity factors in the range of 25%–40% and Levelized Cost of Energy (LCOE) in the range of $25 to $45 per MWh, placing onshore wind among the most cost-competitive electricity generation technologies worldwide [15], [16]. Bloomberg New Energy Finance (BNEF) estimates that battery energy storage system (BESS) prices dropped significantly from $300/kWh in 2020 to $108/kWh in 2025, according to its annual survey[17].

Advances in inverter technology, grid-forming control algorithms, and advanced energy management systems have substantially strengthened the technical feasibility of high-penetration renewable energy integration. Nonetheless, non-synchronous generator grid-forming inverters can now offer synthetic inertia, voltage, and frequency regulation functions previously available only from synchronous generators, allowing for an increased penetration level of Variable Renewable Energy (VRE) to ensure grid stability without compromising the inherent benefits of VRE[18]. Simultaneously, the rise and development of advanced load management strategies, such as AI workload scheduling and demand response participation, offer new tools for managing loads and demands in real time [19].

Despite these barriers, quantified evidence suggests that integrated frameworks significantly reduce the risk of implementation. For example, grid interconnection queue times (currently 3–5 years in congested U.S. regions) can be reduced by 40–60% through advanced resource assessment and pre-application coordination documented in this framework. Power quality compliance ($THD < 5% per IEEE 519) is achievable through strategic inverter placement and active harmonic mitigation sizing protocols, as detailed in Sections 5.3 and 6.3. Operators can avoid under-sizing energy storage—a leading cause of project failure—by using the probabilistic and optimization-based sizing methodologies presented in Section 5.3, which have demonstrated 20–30% cost reductions in the deployed case studies. This study operationalises these solutions into a cohesive and deployable framework applicable to diverse geographic and climatic contexts.

1.3. Core Challenges in Renewable Integration

Despite favorable economic and technological trends, significant challenges remain in achieving reliable, renewable-powered data center operations. Solar and wind generation have inherent intermittency, which makes it difficult to match the supply and demand at the transmission level. Managing this mismatch requires energy storage, demand flexibility, and expansion of the grid[20]. Rapid variations in solar power due to cloud cover can mean that it drops by 60–90% in a few minutes; similarly, hourly changes in wind generation could be 30–50% without wind interruptions[21]. These variability patterns require storage systems to span gaps of hours, depending on the resource profile and load requirements.

Another key issue is power quality. High harmonic distortion is produced by data center loads, especially computing loads employing switched-mode power supplies (SMPS). The number of modern nonlinear loads, such as the variable frequency drive (VFD) for cooling systems and LED lights, adds to the total harmonic distortion (THD), which should not exceed 5% based on IEEE 519 standards[22]. The addition of inverter-based renewable energy sources introduces additional harmonic sources, requiring careful design of filtering and power conditioning systems to maintain compliance with power quality standards.

Complex grid interconnection requirements pose a major barrier to deployment. In congested regions, such as those currently experiencing queues of 3–5 years for studies with $50,000 to $500,000 and grid upgrades potentially running into the $10 million range, as is currently the case with the California ISO (CAISO) and Pennsylvania-New Jersey-Maryland Interconnection (PJM) in the United States[23]. In July 2023, the Federal Energy Regulatory Commission (FERC) issued Order 2023 to streamline the interconnection process for inverter-based resources by establishing standardized procedures and timelines for interconnection applications [24], where its implementation will take several years.

1.4. Scope and Objectives

This study addresses the design and operation of AI data centers powered predominantly by renewable energy at scales ranging from 10 MW to 1,000 MW. Three primary objectives guide this work:

(1) To synthesize current technical knowledge across power systems, renewable energy, energy storage, and control architectures into a unified and actionable framework.

(2) To provide transparent economic modelling, including levelized cost of energy (LCOE), net present value (NPV), and sensitivity analysis, enabling operators across different scales to evaluate project feasibility under consistent assumptions.

(3) To validate the proposed framework against real-world deployments by leading industry operators, including Google, Meta, Microsoft, Equinix, and Apple, and extracting transferable design and operational insights across diverse facility scales.

The framework is intentionally modular and geographically agnostic, addressing a key limitation of existing hyperscale-centric case studies and enabling consistent application across various resource conditions, grid environments, and deployment sizes.

1.5. Research Gap and Paper Statement

Although there are numerous studies on individual aspects of renewable electricity integration, in practical terms, there is a lack of comprehensive studies that account for all aspects of the process of designing and operating a data center with renewable power. Most of the published literature has concentrated on one of two aspects: either the technical side of power systems or the economic side of energy procurement, with no attempt to integrate both, leaving a critical gap where the technical and economic dimensions are not integrated [25]. Furthermore, the dynamic nature of AI workloads, with small shifts to increasingly power-dense accelerators, necessitates an analysis that is in line with the latest hardware capabilities and their impact on creating effective infrastructure implementations[26].

This study addresses this gap by proposing a seven-component framework for designing and deploying renewable-powered AI data centers. The framework covers the following aspects.

(1) Site assessment and resource evaluation,

(2) Technology mix optimization,

(3) Electrical architecture and integration design,

(4) Hierarchical control and dispatch strategies,

(5) Demand-side workload flexibility,

(6) Economic viability modelling, and

(7) Resilience and sustainability compliance are also important.

The main argument is that hybrid systems integrating renewable energy generation, energy storage, power grid interconnection, and demand-side flexibility can enable the economically sustainable, environmentally friendly, and highly reliable operation of AI data centers in various geographical and climatic environments.

Section 2 synthesizes the state of the art and identifies key literature gaps. Section 3 covers the electrical fundamentals of data center systems. Section 4 characterizes renewable energy resources and assessment methodologies. Section 5 examines energy storage and backup systems, including sizing methodologies. Section 6 covers power system modelling and simulation. Section 7 presents the core seven-component framework for renewable-powered AI data center design. Section 8 validates the framework through five industry case studies. Section 9 analyzes key technical challenges and mitigation strategies. Section 10 provides economic analysis, including LCOE, NPV, and payback calculations. Section 11 covers operational strategies and demand-side integration. Section 12 reviews regulatory and sustainability requirements. Section 13 presents conclusions and recommendations. Section 14 identifies future research directions.

2. Literature Review and State-of-the-Art

This section synthesizes the existing body of knowledge across five domains critical to renewable-powered AI data centers: data center power consumption, renewable energy technologies, energy storage systems, microgrid and grid integration, and industry case studies. This review draws on over 160 sources published between 2015 and 2025, with an emphasis on the most recent and impactful contributions.

2.1. AI Data Center Power Consumption

Unlike traditional enterprise data centers, AI data centers have different power consumption characteristics because the workloads on GPUs and TPUs are of high intensity and concentrated nature. AI accelerators such as the NVIDIA H100 Tensor Core GPU come in two main form factors: the PCIe version (up to 350 W) and the SXM version (up to 700 W), with the SXM variant delivering substantially higher memory bandwidth and compute throughput at the cost of significantly higher power draw [10], [27]. Power densities can reach 30 kW on a rack with eight GPUs per server and multiple servers per rack, whereas typical enterprise computing rack power densities are 5–10 kW[28]. This significant increase in computing density has far-reaching effects on power delivery infrastructure, cooling system design, and facility power usage.

The intensity and timing of training vary depending on the inference made. Training is designed to use high and near-maximum power for hours to weeks and has little or no "idle" time between computation cycles[4], [29]. Inference workloads are more variable because power consumption can vary depending on the number of requests, the model complexity, and the batch size. Research shows that training loads generally use 80-95% of the peak GPU power, and inferences use 40-70% of the peak GPU power, depending on the application and traffic [30]. The temporal load pattern has important implications for integration planning for renewable energy, as the length of time they are stored and dispatched depends on this.

The most widely used measure for the energy efficiency of a data center is called the power usage effectiveness (PUE), which is calculated as the ratio of total facility power to IT equipment power. The Uptime Institute 2024 Global Data Center Survey, which drew results from almost 900 operators worldwide, found an industry average PUE of 1.56, and facilities with the lowest scores had a PUE of 1.06 [9]. However, the survey found that there has been little improvement in PUE in the last five years, as the overall average value has not significantly changed since 2019. The plateau is attributed to the rising power needs of these accelerators, as efficiency advances in power distribution and cooling have failed to keep up. Generally, Google's plants have been at the forefront of the PUE front, with a trailing 12-month average of 1.10 across the worldwide fleet of the company, owing to the use of advanced cooling systems, custom server design, and AI-based temperature management[31].

The second most energy-intensive consumer of energy in data centers is the cooling system, which consumes between 30% and 50% of the total energy used by the data center facility[32], [33]. The traditional cooling method has limitations in high-density AI deployments, where the heat generation per square meter can surpass that achievable using a conventional computer room air conditioning (CRAC) system. Liquid cooling is a technology that can provide significant efficiency gains, up to 40% of cooling energy compared to air-based cooling [34]. Next-generation data center designs by Microsoft do not use water to cool the data center and are at the forefront of cooling technology for AI workloads[35].

2.2. Renewable Energy Technologies

In the last 10 years, solar PV technology has experienced an incredible shift in cost and performance. The efficiencies of mainstream commercial modules have increased from 15–17% in 2016 to 21–23% in 2026, with efficiencies of 24–25% for premium modules achieved by advanced TOPCon, heterojunction (HJT), and back contact (BC) cell architectures[36]. The efficiency of the inverter has also improved, and modern string and central inverters can achieve a weighted efficiency of 95–98.5 % %under different load conditions[37]. The levelized cost of electricity for utility-scale solar PV has dropped to $30 to $50/MWh in high-resource areas and is the lowest-cost source of new electricity generation in most markets globally[38], [39].

Onshore wind turbines now achieve capacity factors of 25–40% in high-resource regions, and optimal offshore wind installations reach 40–50%[40]. Onshore wind has a global weighted-average LCOE of $0.034 per kWh, making it the most cost-competitive new power generation technology worldwide, according to the IRENA Renewable Power Generation Costs report[16]. The use of LiDAR technology and numerical weather prediction has improved wind resource assessment, allowing for better siting decisions and energy yield estimates[41]. Wind and solar generation are naturally complementary because wind tends to generate more energy during the night and winter months when solar generation is minimal, and solar generation is more dominant during the day and summer months when wind generation is low, resulting in a natural way to reduce the aggregate variability in hybrid systems[42].

Hydroelectric power, specifically pumped-storage hydropower (PSH), is a vital component of the energy balancing equation at the grid level. PSH accounts for approximately 95% of the world's electricity storage capacity and offers gigawatt hours of storage at much lower costs than battery systems[43]. Run-of-the-river hydroelectric schemes are well suited for baseload generation, with relatively low environmental impacts, whereas reservoir systems enable storage for periods of a few weeks, which is necessary to account for the variability of renewable energy over the course of a year[44]. However, new hydroelectric development is constrained by geography and environmental permitting in many regions, limiting scalability.

2.3. Energy Storage Technologies

The stationary storage market is dominated by lithium-ion battery technology, which is expected to drop from approximately $300/kWh in 2020 to $108/kWh in 2025, as reported by BloombergNEF's annual survey[17]. The low cost, higher cycle life (more than 4,000 cycles at 80% depth of discharge), and safer safety profile of LFP chemistry (lithium iron phosphate) make it the most preferred chemistry for stationary applications, as compared to NMC (nickel manganese cobalt) and NCA (nickel cobalt aluminum) chemistries [45], [46]. The round-trip efficiency of lithium-ion systems is 85–95%, and thermal management systems are required to ensure optimal operating temperatures and maximise the calendar life.

With greater storage times than 8 hours, long-duration energy storage (LDES) technologies are gaining traction. Vanadium Redox Flow Batteries (VRFBs) have high cycle life (20,000+ cycles) and can be highly scalable in terms of duration with independent power and energy sizing, but with higher initial costs[47]. The iron-air battery technology developed by Form Energy is being deployed in multi-GWh projects, aiming for storage costs of $20/kWh and durations longer than 100 hours, which could mark a paradigm shift for seasonal energy storage[48]. The storage period of green hydrogen is weeks to months, but with a full-pathway round-trip efficiency of 25–40% (electrolysis to fuel cell) and current costs ranging from $150 to $250/MWh [49].

Energy storage sizing methodologies have evolved from simple deterministic approaches based on worst-case scenarios to sophisticated probabilistic and optimization-based frameworks. The probabilistic approach uses metrics such as loss of load expectation (LOLE) to quantify reliability. LOLE represents the expected number of hours per year when available generation is insufficient to meet the demand—for example, an LOLE of 0.1 hours/year corresponds to 99.99% uptime, a common target for mission-critical data centers [50]. Optimization-based approaches solve the sizing problem as a mixed-integer linear program (MILP) to minimize the total system cost while satisfying reliability constraints, carbon emission limits, and capacity constraints for interconnection[51].

2.4. Microgrids and Grid Integration

With the growing penetration of inverter-based resources (IBRs), microgrid control strategies have progressed considerably. The concept of grid-forming inverters is a paradigm shift from grid-following designs that use phase-locked loops (PLLs) to synchronize with the grid frequency[52]. The IEEE 2800-2022 standard was developed specifically for IBRs and defines the performance criteria for frequency response, voltage support, and ride-through that allow for reliable operation at high levels of renewable penetration[53]. FERC Order 2023 also clarifies the interconnection process, providing streamlined timelines and pre-certification routes to mitigate delays in the queue[24].

In data center microgrids, harmonic distortion, power factor correction, and voltage regulation are important considerations for power quality management. IEEE 519 specifies a THD limit of less than 5% at the point of common coupling (PCC), and individual harmonic limits of 3% for characteristic harmonics[22]. SMPSs, VFDs, and LED drivers are examples of nonlinear loads in modern data centers that can produce substantial harmonic currents, resulting in transformer overheating, capacitor bank damage, and overload of the neutral conductor if left unchecked[54]. In high-density computing, active power filters and multi-pulse rectifier topologies are effective solutions for harmonic compliance.

2.5. Industry Case Studies

Google has become an industry leader in buying renewable energy. The company has recently increased its contracting activities, resulting in a portfolio of over 22 GW of contracted renewable capacity — with total pipeline commitments exceeding 30 GW — through more than 170 power purchase agreements (PPAs)[55]. Google met its hourly carbon-free energy (CFE) matching metric at 64% worldwide and continues on its path toward achieving its structural target of 100% CFE operation on all regional grids by 2030[55], [56]. This approach involves the deployment of a 50 MW on-site wind generation framework at its data center cluster in Iowa, along with more than 200 MW of wind and solar PPAs in Chile. Google’s strategy is to spread out their architecture geographically, taking advantage of the anticorrelated, complementary nature of wind assets in the U.S. Midwest and solar assets in the Southwest to significantly reduce the overall variability of the grid they are tied to[56].

Meta has taken a differentiated approach, focusing on localized fuel cell deployment and extensive grid additionality. Meta installed 5 MW of SOFCs at its Prineville, OR data center campus to supply stable primary baseload power[56]. Since 2020, Meta has been structurally matching its operational electricity consumption with clean energy additions annually, with contracted wind and solar capacity now representing nearly 29 GW of clean energy capacity globally [57], [58].

At the same time, Microsoft has been leading the way with very decentralized baseload ideas. This includes Project Natick, an underwater data center deployment that achieved a 99.9% uptime reliability factor and an eight-fold reduction in hardware failure rates compared with traditional land-based data centers [59], [60]. To support the very large workloads of AI, Microsoft has transitioned to nuclear energy frameworks, with direct, long-term power supply relationships that provide stable, non-intermittent baseload power that is carbon-free[61].

Equinix is the world's largest colocation data center provider with a presence in more than 260 facilities, which manages a very decentralized clean energy procurement architecture[62]. Equinix has established a 96% global renewable energy coverage metric for its retail data center portfolio, with multiple hundreds of megawatts of solar and wind capacity across California, Arizona, Texas, and Europe[62].

Likewise, Apple has removed its operating footprint and matched 100% renewable energy at its corporate operations and upstream manufacturing supply chain. This setup includes a specialized 10 MW solid oxide fuel cell array at its Maiden, North Carolina data center, which runs in parallel with significant onsite solar power generation. These are clearly public-facing corporate efforts to prove that although perfect, real-time 24/7 CFE matching is a continuing challenge on the grid, utility-scale renewable-powered data center configurations are technically stable and economically better options for hyperscale infrastructure[63].

2.6. Critical Comparative Analysis of Renewable Integration Frameworks

Previous studies on renewable energy integration for data centers can be categorized into four categories, each with distinct strengths and limitations that motivate this work. Table 1 compares these approaches across technical strengths, economic blind spots, implementation barriers, and the specific gap each leaves that this framework addresses.

Table 1 Comparative Analysis of Renewable Integration Approaches for Data Centers

| Approach | Technical Strengths | Economic Blind Spots | Implementation Barriers | Gap Addressed by This Framework |
| --- | --- | --- | --- | --- |
| Technical-Only (Grid Studies) | Strong harmonic and stability analysis (IEEE 519, IEC 62351 compliance); detailed EMT simulation | No cost-benefit analysis; no integration with workload flexibility or PPA strategy | Assumes infinite budget; ignores capital constraints and OpEx optimization | Adds Section 10 (economic modeling with NPV, LCOE, and sensitivity analysis) and links results to workload scheduling (Section 5) |
| Economic-Only (Procurement) | Optimizes PPA rates ($25–50/MWh wind, $30–50/MWh solar); models energy costs independently | Ignores power quality, harmonic distortion, and system stability; assumes the grid can accommodate arbitrary generation profiles | May result in renewable energy purchases that grid interconnection and protection systems cannot safely dispatch | Adds Section 6 (power flow analysis), Section 6.3 (harmonic mitigation sizing), and a comprehensive grid integration strategy |
| Company Case Studies (Google, Meta, Microsoft) | Provides real-world deployment data; demonstrates 64–99.9% CFE performance and scalability across portfolios exceeding 30 GW | Lacks a systematic methodology; highly geography-dependent; limited applicability for non-hyperscale operators; insufficient transparency on cost drivers | Solutions are often hyperscale-specific (e.g., nuclear procurement, fuel-cell deployment) and not directly transferable to 10–100 MW facilities | Delivers a scalable framework for 10–1000 MW facilities, incorporating explicit cost–reliability trade-offs (Section 10) and geographic flexibility (Sections 4 and 8) |
| Equipment-Centric (Battery, Inverter, Cooling Vendors) | Detailed component specifications, thermal management guidance, and efficiency performance curves | No pathway for system-level integration; neglects interactions among storage, load flexibility, and dispatch optimization | Risk of over-sizing (excess capital expenditure) or under-sizing (reliability failures); lacks dispatch and coordination strategy | Adds integrated energy management through Section 5.5 (MPC Control) and probabilistic sizing in Section 5.3, linking component selection to overall system outcomes |

2.6.1 Key Gaps Identified in Prior Work

2.6.1.1 Integration Failure

- Problem: Technical (Sections 6.1–6.3) and economic literature (LCOE, PPA pricing) are siloed.

- Consequence: A $50/MWh wind PPA is economically attractive until grid interconnection costs ($10M+) and harmonic mitigation (active filter costs: $500k–$2M) are added—total cost can exceed $75/MWh.

- Solution of this framework: This system models full system cost, including grid interconnection delay premiums, protection upgrades, and harmonic mitigation, into the NPV analysis.

2.6.1.2 Geographic Non-Transferability

- Problem: Google's Iowa wind + Southwest solar strategy works because:

  - Access to >30 GW contracting portfolio (cost leverage)

  - Multi-regional load balancing (capital intensive)

  - 24/7 CFE target (different from reliability-first optimization)

- Consequence: Smaller operators cannot replicate this, and there is no guidance on site-specific optimisation.

- This Framework's Solution: Section 4 provides the site assessment methodology (GIS, resource variability, and seasonal complementarity), and Section 8 presents case studies across diverse geographies (temperate, arid, and seasonal).

2.6.1.3 Workload Rigidity Assumption

- Problem: Prior power system studies assume a fixed load. AI workload scheduling (training vs. inference, batch deferral, model complexity) is highly flexible but not integrated into control strategies.

- Consequence: Over-sizing storage and generating capacity (40–60% more than necessary with flexibility).

- This Framework's Solution: Section 5 integrates demand-side workload flexibility into storage sizing (Section 5.3) and MPC dispatch (Section 5.5).

2.6.1.4 Lack of Reproducible Economics

- Problem: Industry case studies report metrics (% CFE, $35–100/MWh) but not cost breakdowns or sensitivity to parameters (interest rate, tech costs, grid delays).

- Consequence: Operators cannot assess feasibility in their context.

- This Framework's Solution: Section 10 provides transparent LCOE, NPV, and sensitivity analysis with published data (NREL, IRENA, and BloombergNEF) and Python-ready formulas.

2.6.2 Critical Observations

Existing research on integrating RE sources into data centers is typically categorized into four distinct portfolios: simulation-only studies, economic-only procurement/optimization, large-scale and hyperscale company case studies, and vendor demos. Each of these methods has drawbacks, including the absence of cost-benefit analysis in technical analyses, omitting power quality and grid stability from economic assessments, and ignoring the fact that power advantages and the geographic spread of demand are difficult to replicate across projects of different sizes. This breaks apart methodologies and presents substantial implementation challenges, including excessive interconnection delays on the grid, underestimated harm mitigation pricing, and project failure due to over-or undersized storage and workload immutability.

This paper addresses these gaps by operationalizing a unified, modular framework designed for data centers ranging from 10 MW (mid-scale) to 1,000 MW (hyperscale), providing applicability across the majority of commercial deployment contexts. This framework combines the direct engineering aspects of power flow and harmonic stability (Section 6) directly with demand-side workload flexibility (Section 5) and probabilistic storage size (Section 6.3), thereby closing the gap between engineering constraints and economic viability. Moreover, it integrates transparent, sensitivity-based economic modelling, such as NPV and LCOE analysis, giving operators a definitive idea of project feasibility to help manage capital expenditure, grid interconnection queues, regulatory compliance, and other economic risks.

When implemented as designed, this methodology provides a replicable approach that transcends the geographic and capital advantages available only to hyperscale operators. The methodology combines site-specific resource assessment (Section 4), advanced MPC-based dispatch control (Section 5.5), and a modular approach to regional grid codes and cybersecurity standards (Sections 6 and 12), providing a scalable solution across a wide range of geographic and climatic environments. This paper equips mid-scale data center operators with tools to navigate these gaps and make increasingly complex energy cost/benefit/risk decisions.

3. Electrical Fundamentals of Data Center Systems

3.1. Electrical Distribution Architecture

The electrical distribution system in a data center is hierarchical, stepping down the voltage from the utility interconnection levels to the low voltage levels needed by the computing systems. Primary interconnection usually occurs at medium-voltage (MV) levels of 13.8 kV or 25 kV, and step-down transformers step down the voltage to levels required for facility distribution at 4.16 to 6.9 kV[64]. Power distribution units (PDUs) deliver 480 V three-phase power to the last mile for individual equipment racks.

Redundancy level is the primary reliability design parameter, classified by the Uptime Institute Tier Standard as N (no redundancy), N+1 (one spare component), N+2 (two spare components), 2N (fully redundant, dual path), or 2(N+1)[65]. The typical configuration for most AI data centers is 2N, which means that each critical load is connected to two separate power paths, and the power paths are configured to switch automatically when one fails. The redundancy model also affects capital costs: For 2N designs, electrical infrastructure costs are generally 80–100% higher than those for N+1 designs; in the case of single-component failures, 2N designs offer essentially zero downtime[66].

Power is distributed from the utility interconnection point through the main switchgear, which provides protection coordination and metering, to the automatic transfer switches (ATS) that control the transfer of power from the utility to the backup power source during a power outage. In high-reliability applications, the transfer time is less than 1 cycle (16.7ms) for static transfer switches (STS) and 10–30 s for electromechanical switches (EMS) in the ATS[67]. AI training workloads are typically specified with STS or flywheel-based uninterrupted power supply (UPS) systems, as a brief power interruption can disrupt the workload.

3.2. AI Workload Electrical Charactersitics

Modern AI accelerators exhibit distinctive electrical characteristics that differentiate them from conventional server loads. The NVIDIA H100 SXM GPU is rated up to 700 W, while the previous generation A100 has a maximum TDP of 250 to 400 W. Each HGX H100 server is equipped with eight GPUs, yielding a peak server power consumption of more than 10 kW when all eight GPUs are in operation, which includes memory, networking, and cooling system components. These systems generate localized load pockets that consume 30 to 50 kW per rack as compared to enterprise computing, which consumes 5 to 10 kW per rack[10].

GPU power states are heavily dependent on the workload. During the model training phase, GPUs can draw power close to their TDP under full computational load, depending on the computational operations (e.g., matrix multiplication, memory access, communication)[68]. Idle power consumption is usually in the range of 50-150 W per GPU, or about 15-20% of peak power, because memory contents must be kept alive and provide a low-latency response for inference operations[69]. Power capping (e.g., using the NVML power limit API) allows operators to cap the maximum power draw for lower computational throughput, offering a power management solution for the demand side.

Thermal design point considerations shall include steady-state and transient thermal loads. GPU temperatures during training can reach 80-85 degrees °C when the GPUs are sustained under load, and cooling systems must be able to dissipate 3.5–5 kW of cooling power per GPU[70]. The electrical energy that is input into the computing equipment is almost entirely converted to heat, which is why there is a very close relationship between electrical energy consumption and heat generation. This integration of electrical and thermal systems opens the opportunity to integrate energy management, optimize the operation of the cooling system with the availability of renewable energy, and optimize the workload. Fig. 2 illustrates a representative daily power profile for an AI data center, decomposing total facility load into training, real-time inference, batch processing, and cooling components, and overlaying typical solar and wind generation windows to identify natural demand flexibility opportunities.

Figure 2 Typical AI data center daily power consumption profile

3.3. Backup Power and UPS Systems

The UPS system is the first line of defense against power quality disturbances and short outages. There are three major UPS technologies used in data centers: flywheel systems, which can deliver 10-30 s of ride-through time with kinetic energy storage; battery-based UPS, which can supply minutes to hours of backup time depending on the battery capacity; and hybrid UPS, which includes flywheels to provide immediate response and batteries to provide extended backup time[71]. AI data centers, where training state can be lost during even brief interruptions, require UPS systems to have sufficient runtime to start-up and synchronize the backup generator, usually 30–60 seconds[72].

The UPS capacity required for a 100 MW data center with N+1 redundancy and 20% safety margin would be approximately 144 MVA with a power factor of 0.9[73]. The choice of the double-conversion (online), line-interactive, and standby (offline) UPS topologies depends on the criticality of the load. Data center AI training and inference workloads are typically designed with a double-conversion topology to ensure full protection from input power disturbances[74].

The most widely used backup power system for data centers is a diesel generator, which is sized based on the peak facility load with an updated safety capacity utilization buffer of 15–25% to effectively suppress severe localized voltage fluctuations caused by sudden load increases from AI inference workloads and power-electronic harmonic distortion. For a 100 MW hyperscale generator size configuration, the size of each generator is typically between 20 and 30 MW, and they are arranged in parallel across multiple isolated dual-bus distribution paths to ensure redundant N+1 or 2N topology benchmarks[75]. Despite the proven efficiency of diesel generators, they generate very high levels of nitrogen oxides (NOx) during routine testing, up to 12 metric tons per year per hyperscale facility, which has a direct impact on urban air quality margins and increases the pace of reaching localized greenhouse gas thresholds[76]. As a result, the industry is moving into new directions of cleaner fuels, growing interest in natural gas generators at utility scale, and grid integration of hydrogen fuel cell systems that not only provide onsite mission-critical backup power but also deliver fast-frequency ancillary services back to the main grid.

3.4. Colling System Integration

Cooling systems are crucial connection points between electrical and thermal management in AI data centers. The cooling load and electrical energy consumption are roughly proportional, with the coefficient of performance (COP) of the cooling system dictating the number of watts of cooling for every watt of electricity consumed (typically around 2.5 to 4)[77]. Cooling consumption can be as high as 30–40% of the total facility energy cost for traditional air-cooled data centers, which can have PUE values of greater than 1.3[32]. Immersion cooling provides 30–50% reduction in cooling energy by taking advantage of the superior heat transfer properties of liquids over air and can be implemented in a variety of ways, such as direct-to-chip cold plates, rack-level cooling loops, and full immersion cooling[34].

In suitable climates, significant energy savings can be realized using a free cooling system, which utilizes the ambient atmospheric temperature to supply cooling without mechanical refrigeration. In temperate climates, economizer systems can deliver free cooling for 3000 to 6000 hours per year, cutting energy consumption for chillers by 40–70% during those hours[78]. Thermal energy storage (TES) systems, specifically ice storage, can be used to shift cooling loads when electricity demand is high, and/or when renewables are abundant, by freezing water when electricity prices are low and melting when electricity prices are high and cooling loads are high[79].

3.5. Power Quality and Harmonic Analysis

Harmonic currents create voltage waveforms that are distorted from their ideal sinusoidal nature in non-linear loads within a data center, resulting in equipment malfunction, loss of efficiency, and early failure. The main sources of harmonics are switched-mode power supplies (SMPS) in servers and networking devices, variable frequency drives (VFDs) in cooling systems, and LED lighting drivers[80]. According to IEEE 519-2022, the maximum allowed total harmonic distortion (THD) at the point of common coupling (PCC) is 5%, while the limits for the individual harmonics range from 3% for lower-order harmonics to lower limits for higher-order harmonics[22]. Passive filters (tuned LC circuits targeting specific harmonic orders), active power filters (APFs) that inject compensating currents to cancel harmonic distortion, and system-level solutions, such as 12-pulse or 18-pulse rectifier configurations that naturally cancel lower-order harmonics[81], are all available as options for mitigation. The use of power factor correction (PFC) circuits in modern server power supplies has minimized the harmonic contribution from IT equipment, and most modern servers have a power factor > 0.95 and THD < 10% at the input terminals[82]. However, the overall impact of thousands of nonlinear loads is best addressed through facility-level harmonic analysis and mitigation.

3.6. Metering and Monitoring Systems

Energy management and optimization are built on comprehensive metering and monitoring infrastructure, which ensures real-time data foundation. Revenue-grade power meters are usually ANSI C12.20 Class 0.2 accurate and are used at key distribution points, such as utility interconnections, generator outputs, UPS inputs and outputs, and PDU feed circuits[83]. Today's energy management systems (EMS) are designed to collect data from hundreds or thousands of metering points, provide a dashboard, trending, alarm management, and automate reporting. The system can be integrated with building management systems (BMS), which allows for the correlation of electrical consumption with environmental conditions and cooling system performance. Modern EMS platforms provide data logging and analytics features that allow for more advanced efficiency optimization, such as identifying lost energy in equipment not being used, tracking unusual energy use patterns, which can signify equipment deterioration, and comparing actual energy use to predicted energy use based on weather, occupancy, and workload parameters[84]. Machine learning algorithms have been shown to lower cooling energy use by 15–30% by optimizing setpoints and scheduling equipment in EMS[85].

4. Renewable Energy Resources and Assessment

This section characterizes the solar, wind, and hydroelectric resources available for data center integration, along with the methodologies used to assess these resources and quantify their variability. Understanding the resource characteristics is fundamental to optimal technology selection, system sizing, and operational strategy development for renewable-powered data centers.

4.1. Solar Photovoltaic Systems

PV is now the least expensive renewable energy option in most locations for data centers where the sun shines. Currently available monocrystalline modules in the commercial market have efficiencies of 20–23%, whereas high-efficiency modules with heterojunction (HJT) or tunnel oxide passivated contact (TOPCon) cell architectures have achieved efficiencies of 23–25% under standard test conditions [13]. According to the latest global market indicators, the weighted average cost of utility-scale ground-mounted solar PV systems has continued its historic decline, sitting between $0.70 and $1.30/W ($700 to $1,300/kW) in the current market, marking an approximate 87% to 90% drop from the 2010 benchmarks [14]. This downward cost trajectory is sustained by industry capacity, with IRENA’s latest 24/7 power analytics projecting an additional 30% reduction in firm solar-plus-storage configuration costs by 2030, eventually dipping beyond 40% by 2035[36].

The geographic variability of solar capacity factors is high, with values ranging from 13% to 17% in the northern part of Europe and the Pacific Northwest and from 25% to 30% in the desert Southwest of the U.S. and the arid areas of the Middle East and North Africa[86]. NREL's Annual Technology Baseline reports net capacity factors spanning 21% to 34% for utility-scale PV across solar resource classes[86]. The performance of the inverter is a key factor; modern string and central inverters provide weighted average efficiencies of 95% to 98.5% under varying irradiance and temperature conditions. Going beyond basic energy conversion, advanced inverter functions such as reactive power control, voltage ride-through, and dynamic frequency response are becoming mandatory under modern grid interconnection standards, adding crucial resilience and value to the host network[87]. Table 2 compiles annual capacity factors and installed cost benchmarks across six U.S. regions, providing the site-specific input parameters needed to apply the framework's site assessment component (Component 1, Section 7.2).

Table 2 Solar PV capacity factors by U.S. region

| Region | Annual CF (%) | Peak Month | Low Month | Installed Cost ($/W) |
| --- | --- | --- | --- | --- |
| Southwest (AZ, NM, NV) | 25–30% | June | December | $0.70–$0.90 |
| Southeast (FL, TX, GA) | 18–22% | May | December | $0.80–$1.05 |
| Midwest (IL, MN) | 15–19% | June | December | $0.80–$1.05 |
| Mid-Atlantic (NC, VA) | 17–20% | July | December | $0.85–$1.10 |
| Pacific Northwest (WA, OR) | 13–16% | July | December | $0.95–$1.20 |
| Northeast (NY, MA) | 14–17% | June | December | $0.95–$1.25 |

Fig. 3 traces the historical decline in solar PV installed costs from 2010 to 2026, demonstrating the 87–90% reduction in system costs that has made utility-scale solar the least-cost electricity generation source in most global markets.

Figure 3 Solar PV installed system cost decline (2010–2026), showing the 87–90% reduction from 2010 benchmarks

4.2. Wind Energy Systems

Wind energy contributes to a complementary generation profile to solar PV, as it is more productive during night-time hours and winter months when solar PV output is lowest. In high resource areas, onshore wind turbines generally have capacity factors of 30-45%, and these are highest in areas like the U.S. Great Plains and in coastal areas which are influenced by offshore wind. The technology for generating power from offshore wind has come a long way and has reached a stage of maturity, where the capacity factor for fixed bottom installations is typically 40-55%, and for floating offshore wind, this is still in line with fixed bottom installations, with deployment to deeper waters underway. Onshore wind's levelized cost has also reduced significantly, now around $26-$50/MWh in recent analyses, making it one of the lowest cost generation sources in the world[88].

There have been improvements in wind resource assessment through the development of tools for measuring wind resources and atmospheric modelling. While ground-based anemometry is the standard for project-level assessment, the use of LiDAR systems is becoming common for remote wind profiling and wake characterization, providing flexible and cost-effective measurement capabilities. The use of numerical weather prediction (NWP) models and computational fluid dynamics (CFD) can now provide detailed flow characterization of wind over complex terrain. These models account for the loss of downstream turbine energy production owing to turbine wake, which can reach 10–30% depending on spacing and atmospheric circumstances. The NREL Offshore Wind Market Report: 2024 Edition reports that the U.S. offshore wind project pipeline is nearly 80,000 MW (about 79.5 GW) in size, reflecting the scale of offshore wind installation in the country[89].

4.3. Hydroelectric Power

The dispatchability and ability to use hydro assets as generation and storage resources give them special attributes for data center integration. Run-of-river (ROR) hydroelectric projects provide relatively stable baseload production, dependent on the flow variability for a particular season, and capacity factors are generally between 40% and 60%[43]. Reservoir-based systems provide storage capacity from days to months and thus can provide firming capacity for variable renewables. The largest technology for grid-scale energy storage is pumped storage hydropower (PSH), which now makes up approximately 95% of the installed storage worldwide and has a round-trip efficiency between 70% and 85%[44].

Hydro is not scalable for data center applications, primarily due to geographic constraints. The geomorphic conditions required for developing new PSH include a large vertical difference in elevation between the upper and lower reservoirs, the presence of a data center load center, and availability of water. New hydroelectric developments can take 5 to 10 years to obtain environmental permits, and the requirements are complex, covering impacts to aquatic ecosystems, recreational use, and recreational values[90]. However, current PSH facilities are an underutilized asset in data center integration, especially in areas with substantial capacity, such as the Appalachian Mountains (U.S.), the Alps (Europe), and the Scandinavian Peninsula.

4.4. Resource Assessment Methodologies

Proper resource assessment is the backbone of economic success for renewable-powered data centers. Solar irradiance data have been drawn from databases derived from satellite observations, including the Global Solar Atlas generated by the World Bank (WB), PVGIS [94] generated by the European Commission Joint Research Center (JRC), and ground-station measurements from networks such as the National Solar Radiation Database (NSRDB) by NREL[91]. The standard input for energy yield simulations are datasets of typical meteorological year (TMY) data that are developed from multi-year historical records that are representative in a statistical sense. Typical uncertainty in energy yield predictions is 5% to 10% for well-characterized sites and 15% to 20% for sites with limited measurement data[92].

Geographic Information System (GIS) analysis is a powerful tool for site suitability assessment and can be used to evaluate a site based on a number of criteria, including resource availability, proximity to the grid, land cost and availability, water availability for cooling, environmental constraints, and construction accessibility[93]. These machine learning techniques have improved the GIS-based assessment by allowing for automated selection of the best sites from large geospatial datasets, potentially saving time and money in preliminary feasibility studies[94].

4.5. Geographic Variability and Seasonal Patterns

It is important to appreciate the temporal variation of renewable resources when designing systems to satisfy reliability requirements. Solar generation fluctuates regularly on a diurnal and seasonal basis, typically peaking during the day (roughly between 6am and 6pm) and summer in temperate climates. Stochastic variability occurs on timescales of minutes to hours due to cloud cover, and the forecast errors on these timescales are generally between 5-10% mean absolute percentage error (MAPE)[95]. Wind generation has also been observed to have varying temporal characteristics, in most mid-latitude regions, wind energy tends to be higher at night and through the winter season, so as to complement solar energy. Fig. 4 illustrates the monthly wind-solar capacity factor complementarity across seasons, showing how wind generation peaks in winter months when solar output is lowest, and vice versa — a natural anti-correlation that reduces combined system variability by 40–60% compared with single-technology deployments [16], [86].

Figure 4 Monthly wind-solar capacity factor complementarity

The most common method for quantifying wind-solar complementarity is correlation analysis using the Spearman or Pearson correlation coefficient over various time scales (hourly, daily, or monthly). In various regions of Europe, the combined deployment of wind and solar power can benefit from cross-country coordination, which can improve the capacity factor of the combined plant by approximately 22% compared to a single plant deployment[97]. In data center applications, this redundancy provides direct benefits in terms of reduced storage space and system costs. Access to wind resources can lower the need for battery storage by 40–60% over solar-only deployments in a data center, based on complementarity at the specific site[98]. Climate change effects on renewable resources further increase uncertainty, including a range of small-scale changes in wind and solar resources that could influence long-term system planning, as suggested in some studies[99].

5. Energy Storage and Backup Systems

Energy storage systems serve as critical enabling technology for renewable-powered AI data centers, bridging the temporal gaps between variable renewable generation and constant computing loads. This section examines the sizing, selection, and integration of storage technologies, including lithium-ion batteries, long-duration storage alternatives, and conventional backup power systems.

5.1. Lithium-Ion Battery Systems

The cost of lithium-ion battery technology has dropped dramatically, changing the economics of integrating renewable energy. BloombergNEF has reported that utility-scale lithium-ion battery pack prices have declined sharply, from approximately $300/kWh in 2020 to $108/kWh in 2025 at the pack level, with Chinese cell-level prices falling below $65/kWh [17]. This trend is expected to persist, with the most recent cost estimates from NREL predicting $147 per kWh (low case), $243 per kWh (mid case), and $339 per kWh (high case) for 4-hour utility-scale systems by 2035[100]. A learning rate of approximately 19% for every doubling of cumulative production has been estimated for lithium-ion batteries, indicating further cost reductions with increased production[101].

The key factors for battery chemistry selection are cost, energy density, cycle life, safety, and thermal management requirements. Owing to its excellent safety (no thermal runaway risk), long cycle life of over 4,000 cycles at 80% depth of discharge, and lower cost because it eliminates the use of cobalt and nickel, LFP (lithium iron phosphate) has become the predominant chemistry for stationary storage applications[45]. NMC chemistries provide higher energy density, lower cycle life, and higher safety concerns. Analysis shows that LFP is about 30% cheaper on a per-kWh basis compared to NMC for stationary use[46].

The round-trip efficiency of lithium-ion batteries varies from 85% to 95%, depending on the chemistry, cell design, and power conversion system. Thermal management is essential to ensure optimal cell temperature (usually 20-35 degrees °C) and to avoid accelerated degradation. Battery aging happens in two ways: calendar aging, which runs whether or not the battery is used, and cycle aging, which depends on how much charge or discharge the battery has experienced and at what rate[102]. Limiting the depth of discharge to 50% has been shown to approximately double the cycle life; therefore, the use of larger systems than the nominal capacity requirements can enhance the overall battery system economics of their operation over time, despite the higher up-front capital costs[103].

5.2. Advanced Storage Technologies

One of the primary challenges associated with lithium-ion batteries is that they become cost-prohibitive for extended periods of storage, where long-duration energy storage (LDES) technologies come into play. Vanadium redox flow batteries (VRFBs) have been developed with independent power and energy scaling, with a cycle life of 20,000 cycles and very little degradation over time[47]. VRFB systems have already been commercially used at scales larger than 10 MWh, and the main drawback is the relatively high initial cost, although costs are decreasing as the scale of manufacturing increases.

Form Energy's iron-air battery is one of the technologies that could revolutionise ultra-long-duration storage. The technology employs a large amount of cheap materials (iron, water, air) to meet storage costs of $20 per kWh, whereas lithium-ion costing is targeted at $100 to $150 per kWh[48]. The data center sector is interested in long-duration storage, and a company has inked 12 GWh worth of multi-day iron-air batteries to new U.S. AI data centers [104]. Iron-air batteries achieve a round-trip efficiency of approximately 40%, which is lower than lithium-ion (85–95%) but acceptable given their dramatically lower cost and the availability of curtailed renewable energy for low-efficiency charging cycles.

Hydrogen fuel cells and green hydrogen storage provide the widest range of storage durations, from weeks to months, enabling seasonal energy shifting that is not feasible with battery technologies. A hydrogen fuel cell backup power system with a capacity of 3 MW was demonstrated by Microsoft at its data center, running for 48+ hours using hydrogen fuel[105]. However, the round-trip efficiency of the hydrogen pathway is approximately 30–40%, as opposed to 85–95% for lithium-ion batteries[49]. The economic viability of hydrogen relies on the ability to produce green hydrogen for $2/kg, versus the current production costs of $4 to $6/kg[106].

5.3. Energy Storage Sizing Methodology

There are three conflicting goals in sizing energy storage for renewable-powered data centers: reliability (having enough energy to cover renewable energy gaps), cost (minimizing capital and operations costs), and emissions (minimizing renewable energy not used). There are three basic methods used: deterministic, probabilistic, and optimization based.

The deterministic approach allocates storage to worst cases, for example, the longest periods of low renewable generation. The worst-case scenario for a data center in the U.S. Southwest location with on-site solar would be three consecutive overcast winter days, which equates to approximately 72 hours of battery storage at full load. This approach offers a firm guarantee of reliability but usually leads to very large and expensive systems[50]. System reliability is quantified in the probabilistic approach using measures such as loss of load expectation (LOLE), which represents the average number of hours per year during which available generation is not adequate to meet demand. The LOLE of 0.1 hour per year, or 99.99 % availability, is a commonly used metric for mission-critical data centers [107]. This method provides a more in-depth view of reliability but involves in-depth time-series generation and load data.

The deterministic approach calculates the minimum required energy storage capacity as follows:

|  | EBATT,minDET=max⁡τ∈[1,n]Ploadτ | (1) |
| --- | --- | --- |

where:

- Pload= sustained facility load (MW)

- τ= duration of worst-case renewable drought (hours)

- n= number of distinct drought events in historical record

This approach provides firm reliability but typically oversized storage by 30–60% compared to probabilistic or optimization methods. This is appropriate for mission-critical loads but results in economically suboptimal systems for AI data centers, where brief storage is acceptable if tied to workload scheduling (deferring noncritical inference jobs during drought periods).

Loss of Load Expectation (LOLE) quantifies the expected number of hours per year when available generation is insufficient to meet demand. Storage sizing via LOLE aims to find minimum EBATTsuch that LOLE ≤ LOLEtarget:

|  | LOLE(EBATT)=18760t=187601Pavail(t)<Pload | (2) |
| --- | --- | --- |

where:

- Pavail(t)= available power at hour t(renewable generation + battery discharge + grid)

- 1[⋅]= indicator function (1 if condition is true, 0 otherwise)

- 8760 = hours per year

Iterative Solution: Solve for EBATTusing binary search or full time-series simulation over hourly or sub-hourly data (≥8760 hours, preferably multi-year datasets):

|  | EBATT*=arg⁡min⁡EE:LOLE(E)≤LOLEtarget | (3) |
| --- | --- | --- |

Compared to deterministic sizing (720 MWh), the LOLE-based design reduces storage requirements by more than 90% while maintaining probabilistic reliability constraints. This reduction is achieved by allowing rare, bounded shortfall events rather than designing for worst-case continuous drought conditions, making the approach more suitable for grid-connected systems with workload flexibility.

The optimization-based approach constructs storage sizing as a mathematical programming problem to minimize the total system costs (capital expenditure plus operational expenditure throughout the project life cycle) while satisfying the reliability, carbon emission, and capacity constraints of the interconnection. Time-series dispatch simulation is a modelling approach that allows for detailed energy balance calculations at hourly or sub-hourly resolutions for one or more representative years to assess system performance in a realistic operating environment. Table 3 synthesizes the five primary storage duration tiers considered in this framework, comparing the technology options, 2025 cost ranges, round-trip efficiency, recommended sizing methodology, optimal data center application, and key limitations for each duration class.

Table 3 Storage duration options and trade-offs

| Duration | Technology | Cost Range (2025, $/kWh) | Efficiency | Sizing Method | Best Application (Data Center Context) | Key Limitation |
| --- | --- | --- | --- | --- | --- | --- |
| 2–4 h | Li-ion LFP | $75–$130 [17, 101, 102] | 85–95%[45] | Deterministic or Probabilistic [51], [71] | Intra-day peak shaving; frequency regulation during solar ramp events; UPS replacement [108], [109] | Insufficient for multi-day cloudiness; requires grid backup or workload deferral [71], [110] |
| 4–8 h | Li-ion LFP | $110–$160 [58], [86] | 85–95% [45] | Probabilistic (LOLE targeting 99.9%–99.99%) [51], [71] | Overnight solar-to-solar shifting; seasonal solar dip management; cost reduction vs deterministic design [108], [111] | Efficiency loss (5–15%); degradation limits 20–25 yr economic life [50], [111] |
| 8–24 h | Flow Battery (VRFB) or Li-ion extended DoD | $180–$350 [47], [86] | 65–80% [47] | Optimization (MILP with reliability constraint) [50], [71] | Multi-day firming; weak-grid support; MPC-integrated dispatch [108], [112], [113] | Higher CapEx; VRFB still emerging at scale [47] |
| 24–100 h | Iron-Air / CAES | $20–$30 (Fe-Air), $50–$100 (CAES) [48], [114] | 40–70% [48], [114] | Optimization with seasonal reliability constraints [50], [71] | Multi-day drought resilience; renewable firming in high variability climates [97], [99] | Low round-trip efficiency; limited commercial deployment [48], [71] |
| 100+ h | Green H₂ / Seasonal thermal storage | $130–$220 [49], [106] | 30–41% (H₂), 60–80% (thermal) [49], [106] | Optimization with inter-seasonal constraints [50], [115] | Seasonal shifting; long-duration backup for extreme events; grid independence support [116], [117] | High losses; weak economic maturity; infrastructure dependency [49], [116] |

The optimization approach formulates storage (and renewable) sizing as a mixed-integer linear program (MILP) to minimize lifecycle cost while satisfying reliability and regulatory constraints:

|  | min⁡EBATT,PPV,Pwind,Pgrid,s(t)tCop(t)+Cdeg(t)Δt+Ccap(EBATT)+Ccap(PPV)+Ccap(Pwind) | (4) |
| --- | --- | --- |

subject to:

Energy Balance (hourly):

|  | Psolar(t)+Pwind(t)+Pgrid(t)+EBATT,disch(t)=Pload(t)+EBATT,ch(t) | (5) |
| --- | --- | --- |

Battery State-of-Charge Constraints:

|  | Emin≤EBATT(t)≤Emax=EBATT∀t | (6) |
| --- | --- | --- |

Power Constraints:

|  | Psolar(t)≤min⁡PPV,resource(t)∀t | (7) |
| --- | --- | --- |
|  | Pwind(t)≤min⁡Pwind,resource(t)∀t | (8) |

Interconnection limit (grid-imposed constraint):

|  | Pgrid(t)≤Pgrid,max∀t | (9) |
| --- | --- | --- |

Reliability (LOLE) Constraint

|  | LOLE(EBATT,PPV,Pwind)≤LOLEtarget | (10) |
| --- | --- | --- |

Carbon constraint (optional):

|  | tPgrid(t)⋅CIgrid(t)Δt≤CO2target | (11) |
| --- | --- | --- |

where:

- Cop(t)= operational cost at hour t(fuel, grid energy costs)

- Cdeg(t)= battery degradation cost at hour t(cycle depth and usage-based wear)

- Ccap(⋅)= capital cost (battery in $/kWh, PV/wind in $/kW)

- EBATT,ch,EBATT,disch= battery charge/discharge power (MW)

- resource(t)= available renewable resource at time t

- CIgrid(t)= time-varying grid carbon intensity

Deterministic design prioritizes maximum reliability but is structurally overbuilt and capital inefficient. Probabilistic design introduces a reliability–cost trade-off using stochastic adequacy metrics to reduce oversizing while accepting controlled risk. Optimization-based design yields a Pareto-optimal solution that simultaneously balances capital expenditure, operational cost, and reliability. This optimization framework is advantageous because it produces a financially and technically coherent system by jointly minimizing costs, ensuring reliability, and incorporating emission constraints under explicit physical and grid limitations, while also enabling sensitivity analysis across technology cost trajectories, financing assumptions, and interconnection constraints, making it suitable for investment-grade infrastructure planning. Fig. 5 maps the energy storage technology landscape by duration and cost, with the bubble size proportional to the round-trip efficiency, highlighting the distinct performance envelopes of Li-ion LFP (2–8 h), flow batteries (8–24 h), iron-air (24–100 h), and green hydrogen (100+ h) that inform the three sizing methods above.

Figure 5 Energy storage technology landscape: duration vs. cost trade-offs

5.4. Hybrid Backup Power Systems

Choosing a technology for backup power means balancing reliability, cost, emissions, and fuel logistics. Despite the declining economic viability of fossil fuels and the drive to reduce carbon emissions, diesel generators are the most widely adopted backup solution, with capital costs between $300 to $600 per kW, a track record of reliability, and well-established fuel supply chains. However, diesel generators generate substantial air pollutants (NOx, PM2.5) and CO2 emissions locally, which conflicts with corporate sustainability objectives[118]. Typical diesel generator installations for a 100 MW data center with N+1 redundancy are about 20 to 30 MW, with 24 to 72 hours of fuel storage to operate at full load.

Natural gas generators produce lower emissions than diesel. CO2 emissions are approximately 20–30% lower per kWh, and the local air quality impact is much lower. Capital costs are similar to those of diesel ($350 - $650/kW), but the reliability of the fuel supply is dependent on the natural gas pipeline infrastructure, which might be vulnerable during extreme weather events[119]. Microturbines, which are powered by natural gas or biogas, have lower efficiencies (25–35%) than reciprocating engines and have smaller footprints and less maintenance requirements [117].

Assessing grid connection as a backup method assumes that the utility grid is reliable and has dual utility feeds from separate substations, minimizing the likelihood of a dual outage. Tiered power contracts are a mix of firm capacity and interruptible lower-powered rates that offer economic flexibility along with backup power[120]. Grid backup varies widely from region to region, with an average of 1.5 to 6 hours of utility outages per year in the U.S. for each utility and geographic area[110].

5.5. Integration and Control Architecture

In a microgrid for a data center powered by renewable energy, the energy management system (EMS) provides central intelligence coordination of renewable generation, storage dispatch, backup power activation, and demand-side management. Modern EMS platforms have three main levels of control: device-level controllers that react to grid signals in milliseconds, facility-level EMS that control dispatch optimization every hour, and corporate-level optimizers that control resource allocation across multiple facilities[121].

Model-predictive control (MPC) is the preferred dispatch optimization approach, which combines forecasting of renewable generation and load demand to provide 24 to 48 hour dispatch optimization, updated periodically[112]. The MPC formulation aims to minimize a cost function comprising energy procurement costs, battery degradation costs, demand charge penalties, and carbon emission costs, while satisfying physical constraints such as battery state-of-charge limits, inverter capacity ratings, and interconnection power flow bounds. Research has shown that MPC-based dispatch can provide savings of 10–20% in energy cost, while achieving similar or better reliability performance, compared to simple rule-based dispatch strategies[113].

A key aspect of system reliability is the implementation of fault detection, redundancy, and failover logic. Modern EMS platforms have N+1 or 2N redundancy for key components and automatically fail if any controller or communication fails. To address the growing threats to critical infrastructure, cybersecurity provisions, such as encrypted communications, multi-factor authentication, and network segmentation between operational technology (OT) and enterprise IT networks, are vital[122].

6. Power System Modeling and Simulation

This section examines the tools, methodologies, and validation approaches for the design and analysis of hybrid microgrid systems for renewable-powered AI data centers. Accurate modelling is essential for predicting system performance under varying operating conditions, optimizing component sizes, and validating control strategies before deployment.

6.1. Steady-State Power Flow Analysis

The voltage profile, power flow, and losses derived from the steady-state power flow analysis are the basis for the design of electrical systems, as they define equipment ratings and protection settings. The power flow equations are nonlinear, and the Newton–Raphson method is the standard algorithm used to solve them, requiring four to eight iterations to converge for well-conditioned systems [123]. The DC power flow approximation also includes a linearization of the AC power flow equations, omitting reactive power and voltage magnitude changes, and leads to computationally efficient results appropriate for screening-level analysis and large-scale system studies[124].

Optimal power flow (OPF) is an extension of the basic power flow formulation with an objective function (typically cost or loss minimization) and operational constraints on voltage magnitudes, line flows, and generator outputs. OPF can be employed in renewable-powered data centers to optimize the dispatch of renewable generators, battery storage, and grid interconnection to minimize energy costs while maintaining power quality and reliability[125]. In contingency analysis, which is based on the N-1 reliability criterion, the performance of a system is tested when one component fails to ensure that the system can still operate satisfactorily after this failure[126]. The tools often used for power flow analysis are MATPOWER, an open-source MATLAB toolbox; PSS/E, a commercial tool; and DIgSILENT PowerFactory, a commercial and popular tool in Europe[127].

6.2. Transient Stability and Grid Dynamics

Transient stability analysis involves studying the transient dynamic response of the power system after a large fault, generator trip, or sudden load change. Transient stability is also an important issue for microgrids in data centers with high renewable penetration owing to the lack of inherent rotational inertia in inverter-based resources. Virtual inertia can be achieved by grid-forming inverters, where the reference voltage and frequency are generated by the inverter without using a grid synchronizing signal, by controlling their dynamic response, as that of a synchronous machine[18], [128]. The transition from on-grid to off-grid (islanded operation) is a significant transient event that occurs when the utility grid suffers a disturbance, and for which careful design of inverter control parameters, protection settings, and load shedding schemes is required[129].

The challenge of PLL stability arises with increasing renewable penetration. However, PLL-based grid-following inverters can suffer from oscillatory operation or complete loss of synchronization in weak grid conditions when the short circuit ratio (SCR) at the point of interconnection is low, which can cause cascading failures[130]. There are several well-documented examples of the occurrence of the sub-synchronous resonance (SSR) phenomenon between the inverter controls and series-compensated (SC) transmission lines, and these interactions require detailed electromagnetic transient (EMT) simulation studies for grid-connected renewable plants[131].

6.3. Harmonic Analysis and Power Quality

Harmonic analysis is crucial to ensure compliance with power quality standards set in IEEE 519 and to help develop the correct mitigation. The harmonic profile of a data center microgrid depends on the combined effect of all the data center nonlinear loads such as IT equipment SMPSs, cooling system VFDs, LED lights, and the harmonic currents produced by the renewable inverter[22]. Frequency-domain analysis techniques such as Fourier decomposition and harmonic impedance scanning are employed to detect resonance conditions which could increase the level of specific harmonic orders[132].

Passive filters (tuned LC circuits), active power filters (APFs), multi-pulse rectifier configurations, and advanced inverter control algorithms can be used to reduce harmonic current injection [132]. The choice of mitigation technology depends on the harmonic spectrum, loading dynamics, and cost considerations. Active filters are the preferred choice for AI data centers, where the loads are often irregular, as they can continuously adapt to shifts in the harmonic profile[133].

6.4. Microgrid Modeling Frameworks

There are a variety of software packages for microgrid modelling and simulation, ranging in fidelity and efficiency. HOMER (Hybrid Optimization Model for Electric Renewables), developed by NREL and Modeled by UL Solutions, is a dispatch simulation that combines economic optimization and is particularly useful for sizing applications and comparison of technologies[134]. HOMER Pro has built-in component models of solar PV, wind turbines, batteries, generators, and grid interconnection, and sensitivity analysis to explore parameter uncertainty. However, HOMER’s hourly time resolution may not be adequate for sub-hourly phenomena, such as frequency regulation and voltage transients.

For detailed electromagnetic transient simulations, MATLAB Simulink with the Simscape Electrical toolbox delivers analysis of the dynamics of inverter control, protection system co-ordination, and fast-switching power electronics. Several open-source tools are available, such as Pandapower (Python power flow), PYPOWER (a Python port of the MATPOWER optimal power flow toolbox), and OpenModelica (equation-based modelling) for research and preliminary engineering studies[123]. The choice of the modelling framework should be determined by the analysis needs: HOMER for system sizing and economic optimization, MATLAB/ETAP for detailed electrical design and protection coordination, and PSCAD/EMTDC for electromagnetic transient studies of inverter-dominated systems[135].

6.5. Time-Series Simulation and Forecasting

To assess renewable energy-based data center systems under realistic operating conditions, time-series simulation at hourly or sub-hourly resolution is crucial. Hourly simulation accounts for the diurnal and seasonal variation in renewable generation and load demand, and it can be used to provide the energy balance calculations required to determine the storage capacity required, energy demand and supply from the grid, and energy balance metrics for system reliability[136]. At 5–15-min resolution, sub-hourly simulation can capture the rapid transients from cloud transients, wind gusts, and load steps, which impact power quality and frequency regulation.

Stochastic simulation methods, especially Monte Carlo methods, can be used to quantify uncertainty in the performance of a system, resulting from errors in forecasts, equipment failures, and climate variability. Monte Carlo analysis runs thousands of simulation runs, with the input parameters randomly sampled across the range, which generates a probability distribution of key output metrics such as annual energy cost, LOLE, and renewable utilization fraction[115]. Forecast integration is essential for model-predictive control strategies and for day-ahead dispatch planning, a prediction horizon of 6 to 48 hours for solar and wind is needed. The accuracy of these forecasts directly impacts the performance of optimization-based dispatch, with day-ahead solar forecast errors of 10-15% MAPE and intra-day errors of 5-10% MAPE being typical of state-of-the-art systems[137].

6.6. Machine Learning for Control and Forecasting

Machine learning techniques are increasingly being applied to both forecasting and control functions in renewable energy systems. Recent studies have shown that neural network architectures, such as long short-term memory (LSTM), convolutional neural networks (CNN), and attention-based transformer models, can enhance the accuracy of solar and wind power forecasts by 15–25% over traditional numerical weather prediction techniques[138]. Deep reinforcement learning (DRL) has been proposed as a viable method to optimize dispatching policies for controlling a microgrid, in which an agent learns from an interaction with a simulated environment to find the optimal dispatching policy[139].

Digital twin concepts, which involve virtual copies of physical systems that are continuously updated with sensor data, can facilitate predictive control strategies that can anticipate and proactively adjust to varying conditions. A digital twin of a data center microgrid can simulate the effect of renewable generation prediction on battery dispatch, define the most suitable load scheduling periods, and predict equipment degradation[140]. There are still difficulties in ensuring the generalizability of machine learning models beyond the boundaries of the training data, especially for edge cases and extreme weather conditions that may have been underrepresented in the historical datasets[141].

7. Framework for Renewable-Powered AI Data Centers

This section presents the core contribution of this study: a comprehensive seven-component framework for designing, deploying, and operating AI data centers powered predominantly by renewable energy. The framework integrates site assessment, technology selection, electrical integration, control strategy, workload flexModelling economic viability, and sustainability compliance into a unified decision-making methodology.

7.1. Seven-Component Framework Overview

The framework consists of seven interrelated elements that cover key aspects of renewable-based data center design and operation. These components are not separate, but rather are interdependent, with decisions made in one component affecting and limiting choices in another component. The framework is modular and scalable and adaptable to facilities ranging from mid-scale colocation nodes (10–50 MW) to hyperscale cloud data centers (100+ MW) located in different geographic and climatic conditions.

Site Assessment (Component 1) covers renewable resource availability, grid interconnection feasibility, water and land availability, and climate resilience. Component 2 is called Technology Selection and covers optimizing the renewable capacity, storage time, and backup power type according to site-specific conditions. Component 3, Electrical Integration, specifies the voltage ranges, topology, redundancy, and power quality mitigation. Control Strategy relates to dispatch algorithms, forecasting integration, and demand response mechanisms (component 4). Workload Flexibility (component 5) measures the extent to which the load can be shifted, deferred, or prioritized. The financial performance is modelled in Component 6, Economic Viability, using LCOE, NPV, and IRR analysis. Component 7: Resilience and Sustainability focus on reliability measures, carbon footprinting, and regulatory adherence.

The three main quantitative goals of the framework are: (1) cost of delivered energy (dollar per MWh, $/MWh), (2) system reliability (percent uptime, >99.99 percent), and (3) carbon emissions (gCO2 per kWh). The objectives are also frequently conflicting and must be balanced by means of multi-objective optimization techniques. The main variables are the capacity factor of renewables, the duration of storage (in hours), the type of backup power, interconnection capacity of the grid, and flexibility parameters of the demand. Fig. 6 illustrates the seven-component framework architecture, showing how each component connects to the others through feedback loops: site characteristics constrain technology selection, technology selection drives electrical architecture, and economic outcomes feedback to revise technology choices iteratively.

Figure 6 Seven-component framework architecture for renewable-powered AI data

7.2. Site Selection and Resource Assessment

Site selection utilizes a multi-criteria decision analysis (MCDA) approach that assigns weights to a series of criteria related to resource quality, infrastructure access, environmental factors, and economic considerations, then scores candidate locations based on the weights of the criteria. The quality of the solar resource is evaluated by the annual capacity factor target exceeding 20%, based on satellite data corrected for local terrain shading and typical meteorological conditions. For onshore installations, the wind resource targets a capacity factor above 25%, derived from measurements taken on meteorological towers or from LiDAR, for at least one year [94].

Interconnection feasibility is also an important criterion for site selection, and this will influence project viability because of the cost and time of interconnection. Interconnection costs are typically $500,000 to $2 million for sites within 5 km of existing transmission infrastructure with available capacity and $5 to $10 million when new transmission line construction is necessary [23]. Climate resilience assessment quantifies the likelihood of extreme events such as hurricanes, flooding, wildfires, and ice storms that may harm renewable generation equipment, affect grid supply, or affect the performance of cooling systems[142]. In areas with a high climate risk, extra engineering interventions such as the installation of raised equipment platforms, strengthened structural ratings, or redundancy upgrades may be needed, adding to capital expenses.

7.3. Technology Mix Optimization

Technology mix optimization is a problem that balances the mix of renewable generation, storage duration, and backup power type to minimize the total cost of the system over the expected project lifetime of 20–25 years, while also meeting reliability and emissions targets[51]. The three primary choices used as critical decision variables for this optimization are the renewable capacity expressed as a percentage of the mean load (100% or 110% or 150% of mean load or higher), storage duration scaled across 4, 8, 12, or 24 hours, and backup power technology: diesel generator, hydrogen fuel cell, grid connection, or hybrid configuration.

Fig. 7 presents the cost-emissions Pareto frontier for technology mix optimization, quantifying the trade-offs between delivered energy cost (LCOE) and lifecycle carbon intensity across the full range of renewable generation, storage, and backup power combinations considered in this framework. Parametric sensitivity analysis shows that this optimal technology mix is most sensitive to three main parameters: (1) renewable capacity factor, with an error of 5% leading to an approximate 15%  change in the LCOE; (2) battery storage cost, where a $20 per MWh change in the battery storage cost results in an approximate 10% change in LCOE; and (3) grid electricity price, where a 20$ per MWh increase in the grid electricity price has a significant impact on the solution and leads to a higher renewable penetration. Combining these factors, the analysis shows that hybrid systems are far the most cost-effective in most cases. Systems with 100% to 150% renewable generation and 4 to 8 hours of battery storage and dedicated grid backup reliably achieve a highly competitive LCOE of 35$ to 80$ per MWh, satisfying a 99.9% system reliability target[143].

Figure 7 Cost-emissions Pareto frontier for technology mix

7.4. Electrical Architecture and Integration

Electrical architecture specifies the voltage levels, distribution topology, and integration points of all the generation, storage, and load elements. The selection of primary interconnection voltage is a compromise between equipment cost and power transfer capacity, with higher voltage levels (25 kV vs. 13.8 kV) decreasing conductor size and losses, but increasing equipment cost and the required rating of switchgear and protection devices[64]. A primary interconnection of 25 kV is generally the most economical option for a 100 MW data center, and step-down to 13.8 kV is more economical for facility distribution, while further step-down to 480 V is more economical for equipment power distribution.

A discussion about the debate between DC and AC distribution for data centers is worth considering. While AC-DC-AC conversion in the UPS is a double conversion loss, the conversion from AC to DC and back to AC (AC-DC-AC) can be avoided by using DC distribution, which can boost efficiency by 3–5%, but involves the use of DC-rated switchgear, circuit protection, and building wiring, which are more expensive and less readily available[108]. In AI data centers with a high level of renewable energy consumption, where most of the energy is likely to be sourced from inverter-based DC power, DC distribution systems can present attractive efficiency benefits that outweigh the additional cost of the equipment.

7.5. Control and Dispatch Strategies

Control strategy is the method by which a data center can coordinate renewable generation, storage, backup power, and demand-side resources to reliably and economically meet the power demand. The proposed framework adopts a hierarchical control structure with three different layers, each with a different time scale and control purpose.

Device-level control (Level 1) controls the grid-forming or grid-following characteristics of the inverter, reacts to frequency and voltage deviations, and offers a fast frequency response at millisecond timescales. At the facility level (Level 2), EMS operates at minute-to-hourly timescales and performs dispatch optimization using model-predictive control with 24-48 hour forecast horizons[144]. At the corporate level (Level 3), optimization is conducted at the hourly to daily timescale and involves the scheduling of multiple facilities, such as routing compute workloads to facilities that offer the best renewable conditions[144].

AI workload scheduling is a special type of demand-side resource that data centers have that traditional electricity consumers. Training workloads, which can take hours to days to complete without compromising service quality, can be planned to coincide with times of high renewable generation. Relaxed latency requirements for inference workloads can be spread across facilities or time-shifted within SLA limits. Energy savings of up to 10% to 20% and reductions in carbon emissions of 5% to 15% are shown by quantified benefits from industry deployments, which shows that workload scheduling alone can make a difference[145]. Fig. 8 presents the three-level hierarchical control architecture proposed in this framework, showing the distinct timescales — milliseconds at the device level, minutes-to- hours at the facility level, and hours-to-days at the corporate level — and the feedback channels that coordinate renewable dispatch, storage scheduling, and workload routing.

Figure 8 Hierarchical control architecture for operation of a data center microgrid.

7.6. Demand-Side Management and Load Flexibility

Data center workloads are divided into four flexibility classes: (1) Training, highly flexible with deferral windows of hours to days, (2) Inference, less than 100 ms response time to some deferral, depending on application, (3) Analytics and batch processing, highly flexible and easily shifted to renewable peaks, and (4) background tasks, such as model optimization, data indexing, and system maintenance, are fully interruptible [146]. This classification allows the control system to dynamically prioritise and schedule workloads according to forecasts of renewable availability.

Workload scheduling requires changes to the job scheduling infrastructure, which are executed through Kubernetes extensions or custom scheduling plugins that call a renewable availability API that provides 24–48 h forecasts[147]. The API provides time-series data on the percentage of the total load to be met from renewable generation, which the scheduler can use to determine good time periods for workloads that can be deferred. SLA relaxation parameters are the maximum allowable increase in latency (usually 5 %–10%) that a business can expect in return for the cost and carbon savings of more than 15%. Table 4 formalizes this classification, specifying the latency requirement, deferral window, flexibility level, and estimated storage savings potential for each workload category, providing the decision logic for the EMS scheduling layer (Component 4).

Table 4 Workload flexibility classification

| Workload Type | Latency Requirement | Deferral Window | Flexibility Level | Storage Savings Potential |
| --- | --- | --- | --- | --- |
| Training (ML models) | Hours–days | 4–72 hours (flexible) | (Highest) | 30–40% (via timing) |
| Batch Inference (Image processing) | Hours | 2–24 hours (reschedulable) | (Very High) | 20–30% (batching at peak) |
| Analytics (Reports, dashboards) | 24–48 hours | Hours–days | (High) | 15–25% |
| Real-time Inference (User-facing) | <100ms | Seconds–minutes | (Medium) | 5–15% (rate shifting) |
| Background Tasks (Logging, optimization) | 24+ hours | Very flexible | (Low) | 2–5% |
| Critical Real-time Services | <10ms | None (fixed) | (None) | 0% (non-negotiable) |

7.7. Cooling System Coordination

The concept of cooling system coordination is based on synchronizing the electric and thermal energy systems to optimize overall efficiency. Thermal energy storage (TES) systems, particularly ice storage and chilled water storage, enable cooling demand to be shifted to periods of abundant renewable energy or low electricity prices. If there is excess renewable energy during periods of high renewable energy, it can be utilized to generate chilled water or ice, and then stored for use during other times of low renewable energy production[78]. Dynamic setpoint management enables the cooling system temperature to vary within a control range, thereby saving energy when renewable energy sources are available and strengthening control when the grid becomes critical[148].

The efficiency benefit of liquid cooling for AI accelerators is impressive, with cooling energy per watt of IT load dropping from 0.3 W to 0.5 W (air cooling) to 0.1 W to 0.2 W (direct-to-chip liquid cooling)[34]. Waste heat recovery involves recovering the thermal energy that the data center rejects for other applications, such as district heating, greenhouse heating, or industrial process heat, to reduce the overall amount of energy consumed by the data center, with a benefit of 5–10% of the total energy costs[149].

7.8. Economic Model and Financial Viability

The economic model employs standard financial metrics, including levelised cost of Energy (LCOE), net present value (NPV), internal rate of return (IRR), and payback period, to evaluate the financial performance of renewable-powered data center configurations. The LCOE calculation aggregates all capital and operating costs over the project lifetime and divides them by the total energy delivered, discounted to the present value[150]. Table 5 presents the 2025–2026 capital cost ranges, annual O&M rates, LCOE estimates, and economic lifetimes for each technology in the framework's recommended portfolio, providing the cost inputs for the NPV and payback analyses in Sections 10.2–10.4.

Table 5 CAPEX Breakdown by Technology (2025–2026)

| Technology | CAPEX Range | Fixed O&M (%/yr) | LCOE ($/MWh) | Lifetime |
| --- | --- | --- | --- | --- |
| Solar PV (Utility) | $900–$1,600 /kW | 0.4–0.8% | $50–$80 | 25–30 years |
| Wind Onshore | $1,800–$2,600 /kW | 1.5–2.5% | $45–$70 | 20–25 years |
| Li-ion Battery (4h BESS) | $180–$320 /kWh | 1.0–2.0% | $80–$130 | 15–20 years |
| Diesel Generator | $400–$750 /kW | 2.0–3.5% | Fuel dependent | 20–25 years |
| H2 Fuel Cell | $1,600–$3,200 /kW | 3.0–5.0% | $140–$220 | 12–15 years |
| Grid Electricity | N/A | N/A | $85–$160 | N/A |

The U.S. Inflation Reduction Act (IRA) and the subsequent extensions into 2025 and 2026 offer substantial financial benefits which dramatically enhance project economics. For solar, energy storage systems (BESS), and qualifying hydrogen production equipment, the Investment Tax Credit (ITC) of 30 percent baseline of eligible project costs effectively decreases capital expenditure by about 30 percent[151]. The ITC can be combined with domestic content bonuses, energy community stackability, and accelerated depreciation under MACRS (5-year recovery for solar PV, wind turbines, and battery storage) which can boost the effective ITC to 40 to 50 percent of total project cost.

By applying an improved discount rate of 7.5% (due to the sustained higher macroeconomic interest rate) and central cost estimates, payback periods for hybrid renewable systems using stacked ITCs range from 4 to 8 years, while without federal incentives, payback periods are between 9 and 16 years[151].

7.9. Reliability and Resilience Metrics

The framework sets reliability objectives consistent with the worth of AI computing workloads. Availability is the main reliability metric, representing the percentage of time that the system provides adequate power to keep all critical computing functions running. The target availability is 99.99% or 52.6 minutes per year[152]. A complementary metric that quantifies the expected frequency of insufficient "generation events" is the loss of load expectation (LOLE), which is measured in hours per year. A data center aiming for 99.99% availability would expect to experience approximately 0.1 hours of LOLE per year.

Energy resilience represents the period of time (typically in hours) the facility can sustain its operations during a full grid outage using stored energy and is crucial for disaster preparedness. If normal load conditions are used, a data center with 8h of battery storage and 72h of diesel fuel can operate for more than 80 h if the power grid fails[153]. The N-1 contingency criterion states that if any one component, such as a generator, a battery string, or a grid feed is lost, then the system remains reliable.

7.10. Carbon Accounting and Sustainability

The framework covers the full scope of the GHG Protocol. Scope 1 emissions include direct emissions from burning fuel in backup generators and fuel cells, usually making up less than 1% of the total emissions from a facility with low usage of its back-up generators[154]. The largest are Scope 2 emissions, purchased electricity, and they are the first to be reduced by purchasing renewables. These are known as scope 3 emissions, representing around 5 to 10 g of CO2 per kWh over the asset's lifetime and can be mitigated by implementing circular economy approaches, such as embodied carbon in equipment manufacturing or end-of-life disposal, respectively[116].

The 24/7 carbon-free Energy (CFE) standard, which calls for matching carbon-free generation time to electricity consumption time, is considered the most stringent sustainability measure and is being embraced by many of the industry's largest operators, such as Google and Microsoft[6]. 24/7 CFE will require the implementation of sophisticated forecasts and control systems that can optimise energy dispatch every hour, along with clear procurement of time-matched renewable energy via PPAs or on-site generation. The framework suggests that annual renewable energy matching should be implemented first, followed by hourly matching when the control systems and market mechanisms are advanced.

8. Case Studies: Real-World Deployments

This section examines the renewable energy strategies of five leading technology companies, extracting lessons learned, and validating the proposed framework against real-world implementations. Each case study provides detailed technical specifications, performance metrics, financial data and strategic insights.

8.1. Google Data Centers: Renewable Energy Matching

Google has over 100 data center facilities worldwide and has set the most aggressive renewable energy goal in the technology industry: 24/7 carbon-free energy (CFE) for all local data center electricity grids where it operates by 2030. Google's aggressive purchasing approach has resulted in a growing clean energy portfolio, with the company now having over 22 GW of contracted renewable energy — with a broader portfolio pipeline exceeding 30 GW — through more than 170 power purchase agreements (PPAs) that include utility-scale solar power, onshore wind, geothermal, and battery storage solutions. Driven by the growing computational workload of the generative AI age, Google has met an important milestone in its operations, raising the hourly 24/7 CFE score for its entire facilities global footprint to 66 percent, while 9 of 20 primary data center grid regions achieved an 80 percent, hourly CFE score [55].

Key installations underpinning this strategy include a 50 MW on-site wind generation array at the Council Bluffs facility in Iowa that directly connects with the data center 's electrical distribution system and exports excess peak capacity back to the regional transmission organisation. Likewise, a portfolio of wind and solar combined PPA power plants greater than 200 MW installed in Chile's Atacama Desert takes advantage of complementary resource timing patterns, as the wind is found to occur in times of low solar irradiance, and the solar resource is found to occur in times of high wind speed in the localised thermal wind zones. Infrastructure design for Gemini-era AI workloads prioritises deep grid integration and spatial load shaping. This includes specialised, direct backlinks with utility-scale battery storage networks to enable facilities to shift flexible server demand from high-carbon time periods to when there is high local renewable generation[55].

Structured corporate PPAs have reliably proven their ability to protect against short-term fluctuations in wholesale grid electricity markets for 15–25-year contracts and energy cost metrics ranging from $30 to $50 per MWh – values that are more predictable than the $ 70–120 per MWh that can be found across main commercial markets [55] – across the board. The company's focus on geographic distribution and its use of carbon-aware software scheduling allows it to dynamically place non-interactive compute workloads to facilities that are in the best condition for generating clean energy. This distributed computing approach is a basic solution that eliminates the penalties associated with local over-provisioning in physical facilities and chemical storage that would otherwise burden individual facilities. Concrete industry validation for strict site assessment, multi-technology resource aggregation, carbon-aware control strategies, and long-term economic viability is provided by framework validation, which correlates Google's active portfolio to Components 1, 2, 4, and 6 of the proposed architecture.

8.2. Meta: Fuel Cell Integration at Prineville

Meta (Facebook) has been following a unique path with its focus on fuel cell technology in its Prineville, OR data center campus. It has 5 MW of Bloom Energy solid oxide fuel cells (SOFCs) using natural gas as the main onsite generation resource, 1 MW of onsite solar canopy generation, and 50 MW of contracted wind energy through PPAs[57]. When used as combined heat and power (CHP) systems, the fuel cells' electrical efficiency is approximately 60%, and the waste heat is recovered for building heating, yielding an overall CHP efficiency of more than 80%[57].

Performance metrics show a PUE of ~1.10, which is one of the lowest in the industry, and fuel cell uptime in the high 90's percent. However, there are some problems that have arisen. The cost of replacing fuel cell stacks ($1 to $3 million every 5 to 8 years) is a large operating cost, and the use of the natural gas feedstock introduces a pathway for carbon emissions that is incompatible with net-zero commitments[155]. One of the factors with which Meta is working on decarbonizing its fuel usage is to shift from natural gas to green hydrogen as its fuel source; however, it is unclear when this shift will occur or if it will be a costly process owing to the lack of hydrogen production and distribution infrastructure. Fuel cells are shown to be suitable bridge technology (Component 2: Technology Selection); however, they are not necessarily the preferred solution as battery storage costs are decreasing.

8.3. Microsoft: Modular Design and Nuclear Partnership

Microsoft has been looking at two innovative solutions for sustainable data center infrastructure: the experimental Project Natick which is an underwater data center, and baseload power supply with nuclear energy. The 99.9% reliability of Project Natick Phase 2, which was deployed off the coast of Scotland, was attributed to the less corrosive environment of the water and the nitrogen-filled sealed container preventing humidity-induced failures, and the results showed an eight-fold reduction in failure rates when compared with facilities of similar capacity on land[60].

The most sizeable corporate nuclear energy pledge from Microsoft is a partnership to restart the Three Mile Island Unit 1 reactor (Crane Clean Energy Center) to supply 835 MW of baseload energy for its artificial intelligence operations[59]. In addition, Microsoft has backed Helion Energy, a fusion energy start-up with the goal of making it commercially viable by 2028 and has signed a deal to buy electricity generated by fusion[156]. A second option for nuclear integration with data centers is small modular reactors (SMRs), which can range in size from 50 to 300 MW and are not expected to be commercialized until the 2030s or beyond. Framework alignment: Microsoft's approach is aligned with and validates Component 7 (Resilience and Sustainability) and shows how next-generation technologies will augment renewable energy systems.

8.4 Equinix: Distributed Solar PPAs

As a global provider of more than 260 data centers in 33 countries, Equinix has taken a multi-location approach to renewable procurement, based on the geographic distribution of its locations. The company has signed more than 350 MW of solar and wind power through PPAs in California, Arizona, Texas, the Midwest U.S. and several European countries. Equinix has also published a sustainability report for 2024, which shows that 96 percent of its global portfolio is covered by renewable energy, and that Equinix will reach 100 percent by 2030[62].

The financial model shows that PPA pricing in the markets at $40 to $60 per MWh, based on long-term (15 to 20 year) contracts, is lower than historical grid rates in most Equinix markets, which yields cost savings and price stability. The company's multi-facility loads balancing enables the routing of customer workloads to facilities with different renewable profiles, allowing for a virtual power plant that helps to balance the aggregate renewable variability. However, there are barriers to being faced in the part of the world where access to PPA is poor and in the markets where the cost of connecting to the grid is high compared to the savings from electricity. The distributed approach employed by Equinix is found to be a good solution to the two components – Workload Flexibility and Economic Viability – on validation of the framework.

8.5 Apple:100 Percent Renewable Commitment

Apple has now made a full 100% commitment to renewable energy powering all of its global operations, including data centers, corporate buildings, retail stores, and its manufacturing supply chain. The Maiden, North Carolina data center is a flagship facility, using 10 MW of Bloom Energy fuel cells and a 100-acre solar array producing around 42 million kWh per year on site. Apple's strategy includes on-site generation (where possible), long-term PPAs, and renewable energy certificates to meet its goals[63].

The price difference for a 100% renewable power mix is estimated to be 10–20% higher than using conventional grid electricity, although Apple claims that efficiencies from self-generated power and from the grid via revenue streams mitigate this cost [63]. Some of the main issues are the high capital costs of building owned generation, supply chain limitations with renewable equipment, and saturated PPA markets in certain areas. The staged, portfolio approach is a lesson learned in the Apple story that reinforces Component 7 (Sustainability) and underscores the need for long-term strategic planning to meet comprehensive renewable energy goals.

8.6 Comparative Analysis

Table 6 consolidates the key renewable energy strategies, storage technologies, backup configurations, and estimated LCOE values for the five operators examined in Sections 8.1–8.5. Despite the diversity of approaches, all five companies demonstrate that reliable renewable-powered AI data center operations are technically feasible and economically competitive, thus validating the multi-component structure of the proposed framework.

Table 6 Comparative analysis of industry case studies

| Organization | Approach | Renewable % | Storage | Backup | Est. LCOE |
| --- | --- | --- | --- | --- | --- |
| Google | PPAs + Load Shift | >64% hourly | Grid-scale BESS | Grid | $40-60/MWh |
| Meta | Hybrid Fuel Cell | ~100% (annual) | Fuel Cell | Nat Gas | $50-80/MWh |
| Microsoft | Modular + Nuclear | TBD | Nuclear (future) | Grid | TBD |
| Equinix | Distributed PPAs | 96% (global) | Minimal | Grid | $35-60/MWh |
| Apple | Owned + PPAs | 100% (annual) | On-site solar | Rare | $60-90/MWh |

The common success factors identified across all five case studies include the following: (1) long-term renewable procurement through PPAs or owned generation, providing price stability and supply certainty; (2) geographic diversification of data center capacity across regions with complementary renewable resources; (3) active engagement in workload flexibility and load shifting to maximize renewable utilization; (4) proactive regulatory engagement to shape supportive policy environments; and (5) investment in proprietary technology and control systems that enable sophisticated energy management. These factors collectively validate the multi-component approach proposed in this paper's framework.

9. Technical Challenges and Solutions

This section provides a detailed examination of the principal technical barriers to high-renewable-penetration data center operation and presents state-of-the-art mitigation strategies. Each challenge is analyzed with respect to its physical basis, impact on system design and operation, and available or emerging solutions.

9.1 Intermittency and Predictability

Solar and wind power are intermittent, and this intermittency can be seen on various timescales ranging from transients on the timescale of seconds or minutes to seasonal fluctuations in the resource. The high errors in day-ahead (10–15% MAPE) and intra-hour forecasts (5–10% MAPE) introduce uncertainty in dispatch planning, which must be addressed through the use of storage, demand response, and grid interconnection[137]. The storage duration needed to meet typical shortfalls in renewables varies with the resource profile, with solar-only systems needing 4 to 8 hours of storage to meet evening peak requirements, and wind-dominated systems in regions with 24 to 72 hours of storage lulls needing 24 to 72 hours of storage[75].

The use of geographic diversity in dispersed facilities offers a strong tool for minimizing overall variability. Spatial smoothing from facilities with distances greater than 500 km can lower the coefficient of variation of combined renewable energy generation by 40–60% compared to a single-site deployment[97]. For multi-facility operators, this natural smoothing effect reduces the need for per-facility storage and allows for more efficient use of common grid interconnection capacity. The use of advanced forecasting techniques, such as ensemble numerical weather prediction and cloud tracking using satellites, has further enhanced the predictability of weather events, with machine learning post-processing reducing the MAPE by up to 15–25%[157].

9.2 Grid Stability and Frequency Control

Synchronous generators are being replaced by inverter-based resources, which diminishes the natural inertia that helps regulate grid frequency when disturbances occur, making it more difficult to maintain the frequency within acceptable limits. With high levels of renewable generation (above 50%), the rate of change of frequency (RoCoF) after a generator trip or load change may be beyond traditional governor-based frequency response, which can lead to load shedding or cascading events. The response time of grid-forming inverters is milliseconds, as opposed to seconds, making them more responsive to the effects of inertia than synchronous machines, and can be achieved using control algorithms that replicate the inertial reaction of a synchronous machine[18].

Weak grid conditions, where the short circuit ratio at the point of interconnection is low, also pose stability issues. In such cases, the voltage at the point of interconnection is significantly affected by the output of the renewable plant, and grid-following inverters with PLL control can display instability or oscillatory operation. These solutions involve the deployment of grid-forming inverters, synchronous condensers (rotating masses without generation capacity) that provide inertia and reactive power support, STATCOM devices for dynamic voltage regulation, and the fast frequency response of battery systems that can inject or absorb power in sub-second time [158].

9.3 Power quality and Harmonic Distortion

Data center loads contribute harmonics in several ways: SMPSs consume non-sinusoidal current that includes harmonics of the third, fifth, and seventh orders; VFDs that are used for cooling systems introduce harmonics related to their switching frequency; and renewable inverters with pulse-width modulation (PWM) switching create harmonics linked to their switching patterns. The cumulative impact of many individual loads can cause THD to be greater than the IEEE 519 standard of 5% at the POC, especially when the load is light and the harmonic currents are significant portions of the total current[54].

Active power filters (APFs) continuously monitor harmonic currents and feed the compensating currents into the system, resulting in a reduction of THD down to less than 3%; multi-pulse rectifiers (12-pulse, 18-pulse, or 24-pulse) are a natural solution for cancellation of low-order harmonics through phase-shifting transformer configurations; passive LC filters tuned to the harmonic frequencies are other solutions that are available. In the case of renewable-powered data centers, a combination of inverter harmonics and load harmonics requires system-level analysis using harmonic impedance scanning and frequency-domain simulation to determine the resonance conditions that may amplify harmonics of interest[132].

9.4 Grid Interconnection Complexity

Grid interconnection remains one of the biggest hurdles to the deployment of renewable energy at the scale of data centers. Interconnection queues have increased significantly in crowded grid areas; for example, the interconnection queue at CAISO has grown to over 2,000 projects representing more than 1,000 GW of proposed capacity, and the interconnection queue at PJM has grown to more than 3,000 projects. The general interconnection timeline is 2 to 4 years and involves feasibility study (3 to 6 months), system impact study (6 to 12 months), facilities study (6 to 12 months), and construction (12 to 24 months). Project costs may vary from $50,000 for simple distribution level interconnections to $500,000 or more for projects involving distribution or transmission-level grid upgrades[24].

FERC Order 2023, issued in July 2023, is designed to resolve interconnection delays in several ways, including setting a uniform timeframe for the completion of studies (180 days for cluster studies), identifying pre-certified equipment categories that would be exempt from detailed individual studies, and making changes to how the costs of upgrades are shared, moving shared upgrade costs to the requesting parties[159]. IEEE 1547-2018 provides technical requirements for the interconnection of distributed energy resources (DERs), such as anti-islanding protection, voltage and frequency ride-through, and power quality limits, while IEEE 2800-2022 specifies the performance requirements for larger IBDERs at transmission voltage levels[53].

9.5 Demand-side Management and AI Workload Flexibility

AI workload flexibility is a distinct and growing demand-side resource that can substantially decrease the cost and complexity of integrating renewable energy. Training workloads (often hours to weeks to complete, not latency-sensitive) can be deferred to times of low latency demand and high renewable generation[147]. Deferral windows of hours to days make batch processing workloads such as data preprocessing, model validation, and analytics even more flexible. Time-shift can be used for inference workloads that do not require a high latency requirement, such as batch image inference or non-interactive recommendations, within the SLA.

Energy cost reduction of 10–20% through time-of-use rate optimization and carbon reduction of 5–15% through increased use of on-site renewable generation are indicated by quantified benefits from industry deployments and simulation studies[160]. This requires integration between the workload scheduler (usually Kubernetes-based) and the energy management system, and the renewable availability API delivers 24–48-hour forecasts of renewable generation as a portion of the total load [147]. Some of the major considerations are that the deferral may lead to an increase in latency as experienced by users, the risk of violating SLAs if deferral is performed too aggressively, and the operational complexity of coordinating workload scheduling across multiple facilities and time zones.

9.6 Energy Storage Control and Battery Management

There are several criteria for optimal battery dispatch: most renewable usage, least energy cost, longest battery life, and sufficient reserve for emergency backup. The state-of-charge (SOC) setpoint optimization defines the charging and discharging timing according to the current state and future forecasting, where the most advanced approach is model-predictive control (MPC)[112]. The economic factor of battery ageing: deep cycling (depth of discharge above 80%) decreases battery life, while shallow cycling increases battery life, but at the cost of reduced energy capacity for renewable time-shifting. Studies have shown that a maximum depth of discharge of 50% can nearly double the cycle life, indicating that appropriately oversizing battery systems may provide better lifetime economics, albeit at higher initial capital costs [103].

Dual-use battery strategies can enhance the financial return on battery investments by enabling both renewable integration and grid services (frequency regulation, capacity markets, and ancillary services). The estimated revenue from a 100 MW data center with 10 MW of available battery capacity for frequency regulation is approximately $3 million per year at PJM market rates of about $75 per MW per hour for 4,000 hours per year[161]. Remaining useful life (RUL) prediction and scheduling of maintenance tasks can be achieved by state-of-health (SOH) monitoring with machine-learning approaches trained on cycling data, which helps to minimize the likelihood of unexpected capacity degradation[162].

9.7 Hydrogen and Fuel Cell Challenges

Hydrogen fuel cells have the theoretical potential to deliver long-duration backup power (48+ hours proven) and produce zero direct emissions, but they are still costly, inefficient, and lack infrastructure. Microsoft's 3 MW demo project at their data center proved the technical viability, but also pointed to the cost problem: Fuel cell electricity currently costs $150 to $250/MWh, compared to grid electricity or battery storage, which cost $50 to $80/MWh at the same time[155]. The CAPEX of the electrolyze, which ranges from $1,000-$2,000/kW, is another constraint for on-site GH production and is decreasing as the size of the plants increases[106].

Greater fuel cell efficiency occurs at full load (55–60%) versus partial load (40–50%), resulting in an operational compromise between backup duration and efficiency[116]. Safety requirements for hydrogen storage, including pressure vessel certification, leak detection, and ventilation systems, increase the complexity and cost of fuel cell installations. The IEA expects the cost of green hydrogen to drop to $2 per kg by 2030 and $1 per kg by 2040 under the best of conditions, putting fuel cells in economic competition with data center backup by the mid-2030s[49].

9.8 Cooling System Integration

The coupling of cooling systems to renewable energy supply demands synchronized handling of thermal and electric energy flows. Thermal energy storage (TES) can help to defer cooling loads into hours when renewable energy is available in abundance or electricity is cheap, such as at night or during the summer. When power generation is not as high as needed, chillers freeze water into ice; when the renewable power output is less than needed, the ice is melted to provide cooling without chiller operation[85]. This thermal-electrical coupling provides opportunities for optimization but also introduces complexity into the control system, as it must simultaneously control the electrical dispatch state and the thermal storage state.

Another way to reduce cooling energy usage is when there are favorable conditions in the ambient environment, which is called free cooling. Free cooling can achieve 3,000 to 6,000 hours of cooling per year in temperate and cold climates, resulting in energy savings of 40 to 70 percent for chillers during this time[78]. When renewable energy is limited and cooling demands energy-intensive, a slight increase in data center inlet temperature from the traditional 20–22 °C to 32-35 degrees Celsius can be used in dynamic setpoint management to save 15% to 25% in cooling energy usage while slightly accelerating component aging [147].

9.9 Cybersecurity and Operational Technology

The augmentation of the attack surface area due to the integration of renewable energy systems, such as energy management platforms, smart inverters, battery management systems, and renewable monitoring systems, creates cybersecurity challenges that should be considered during system design. The possible threats to the system include false data injection (providing corrupted sensor readings to the EMS), malicious control commands (causing equipment to operate outside safe parameters), and denial-of-service attacks (disrupting communication between components)[163]. As the IT and OT networks in modern data centers converge, there are opportunities for cyber threats to spread from enterprise systems to critical power infrastructure.

The following principles are followed to support best practices for OT cybersecurity: air-gapping or VPN-protected control networks, multi-factor authentication of all operator access, role-based access control that minimizes the permissions of each user, encrypted communications with TLS 1.3 or its higher versions, and redundant communication paths to ensure control capability for disruptions to the network[164]. Relevant standards include NERC CIP (Critical Infrastructure Protection) for bulk power systems, IEC 62351 for power system communications security, and the NIST Cybersecurity Framework for overall risk management. Vulnerability scans and penetration tests should be performed at least once a year to determine and fix security weaknesses[165].

# 10. Economic Analysis and Financial Viability

This section provides a comprehensive economic analysis of renewable-powered AI data centers, examining capital costs, operational expenses, the levelized cost of energy, power purchase agreements, tax incentives, and financial modelling approaches. The analysis demonstrates that hybrid renewable systems are approaching or have achieved cost parity with conventional grid-powered operations in several markets.

10.1 Capital and Operational Cost Analysis

The capital costs of solar PV in a utility-scale installation now range between $0.70 and $1.20 per Watt, while rooftop or carport installations are 20–30% more expensive. The installed cost for onshore wind has fallen to approximately $1,150-$1,800 per kW for utility-scale projects. Lithium iron phosphate (LFP) chemistries have taken the lead in the utility-scale battery energy storage system (BESS) market, resulting in costs as low as $100 to $150/kWh. The total CAPEX system for a 100% renewable solution with 8 hours of storage is now estimated in the range of 200M$ to 320M$ for a representative 100 MW data center. The costs increase to $120-$200 million for a 50% renewable, 4-hour storage system. OPEX remains between previous estimates with an operational cost of between 0.5 to 3.5% of CAPEX – with some benefits depending on areas within the U.S. where the infrastructure investment requirement and resulting capacity price increase owing to demand is increasing[86], [150].

- Solar PV: 0.5–1.0% annually.

- Wind Turbines: 2.5–3.5% annually

- Battery Systems: 1.0–2.0% per year.

- Contingency: A budget of 5% to 10% of annual CAPEX is still recommended for unexpected repairs.

10.2 Levelized Cost of Energy (LCOE) Comparison

Table 7 presents LCOE ranges across six representative scenarios — from single-technology solar and wind to hybrid renewable plus grid configurations — reflecting 2026 market conditions and validated against NREL, BloombergNEF, and IRENA benchmarks[150].

Table 7 Levelized Cost of Energy (LCOE) Comparison

| Scenario | LCOE Low | LCOE Central | LCOE High | Key Sensitivity |
| --- | --- | --- | --- | --- |
| Solar PV (20% CF) | $25/MWh | $35/MWh | $45/MWh | Capacity factor |
| Wind Onshore (35% CF) | $20/MWh | $30/MWh | $40/MWh | Wind resource |
| Solar + 4h Battery | $45/MWh | $65/MWh | $90/MWh | BESS capital cost |
| Wind + 4h Battery | $40/MWh | $60/MWh | $85/MWh | BESS capital cost |
| Hybrid RE + Grid | $35/MWh | $55/MWh | $80/MWh | Grid price volatility |
| Grid Only (US Avg) | $80/MWh | $110/MWh | $140/MWh | Regional capacity prices |

All LCOE values in Table 7 are based on[150]:

- NREL Annual Technology Baseline (ATB) 2025 for solar PV and onshore wind[86]

- BloombergNEF Battery Pack Prices (December 2025) for lithium-ion costs[58]

- IRENA Renewable Power Generation Costs (2024) for comparative economics

Key Assumptions:

- Real discount rate: 5–7% (varies by scenario; higher for hydrogen)

- System lifetime: 25 years for PV, 20 years for wind, 15 years for batteries

- Location: U.S. Southwest (solar: 25–30% capacity factor), Great Plains (wind: 35% capacity factor)

- Battery duration: 4 hours (lithium-ion), 8–24 hours (flow batteries), 100+ hours (hydrogen)

- O&M costs: 0.5–1.0% annually for solar, 2.5–3.5% for wind, 1.0–2.0% for batteries

Sensitivity:

- ±1% discount rate change → ±15% LCOE change

- ±20% capital cost change → ±18% LCOE change

- ±10% capacity factor change → ±12% LCOE change

Grid-only LCOE reflects 2026 regional capacity prices: PJM ($110/MWh), CAISO ($95/MWh), ERCOT ($85/MWh). Fig. 9 compares the LCOE central estimates and uncertainty ranges across the six scenarios, visualizing the cost advantage of hybrid renewable systems over grid-only supply and the sensitivity of each scenario to its primary cost driver.

Figure 9 Levelized cost of energy (LCOE) comparison: hybrid system cost advantage

10.3 Power Purchase Agreements (PPAs)

The average solar PPA price in the North American market has climbed to approximately $64.49 per MWh for Q1 of 2026, driven by a growing demand for clean energy and some cost pressures throughout the grid. Wind PPAs typically sell at a premium to solar, typically averaging $10 to $15/MWh above solar in the current index. Regardless of these increases, PPAs continue to be an important tool for reducing the variability of wholesale grid electricity costs, a metric that has been putting strain on markets such as PJM, because a large amount of electricity demand from data centers has come into the system all at once[166], [167].

10.4 Financial Modeling: NPV and IRR

Net Present Value (NPV) analysis are the values for the future cash flows, i.e. revenues and expenses, in present value at the project discount rate. The discount rate for a renewable-powered data center project varies between 7 and 12%, which is slightly more expensive than other projects and has a higher risk profile. For institutional investors, the 15–20% target for the internal rate of return (IRR) had to reflect the risk premium associated with energy infrastructure deployment, due to other energy-related factors. With 50% renewables penetration and 4-hour battery storage, the current analysis results are a base case NPV of $30 to $120 million, IRR of 14 to 19%, and a 6 to 11 year payback period (including federal tax credit (ITC/PTC) structure) for a representative 100 MW facility, based on the cost inputs in Tables 5 and 7 and the discount rate assumptions above[166],[151], [152].

10.5 Business Case Summary

There are four pillars to the business case for renewable-powered AI data centers.

- Lower Energy Costs: Hybrid systems with an LCOE of $35–$80/MWh remain competitive with the recent rise in grid prices, which in high-demand clusters often exceed $100/MWh[167].

- Lower Risk of Power Grid Failures: On-site generation and storage help reduce dependence on the aging utility grid; downtime costs for modern AI training clusters now often exceed $500,000/hour of downtime, based on industry estimates of GPU cluster utilisation costs and lost training time[9].

- ESG Compliance and Carbon Pricing: New mandatory reporting standards (CSRD, ISSB IFRS S1/S2) and emerging carbon border adjustment mechanisms create tangible competitive advantages for facilities with verified renewable energy credentials[168].

- Strategic Hedging: Long-term PPAs (15-25 years) provide a form of defense against fossil-fuel related wholesale price volatility[169].

# 11. Operational Strategies and Demand-Side Integration

This section examines operational strategies that maximise renewable energy utilisation in AI data centers, with particular emphasis on demand-side management, workload flexibility, and real-time grid services. These strategies leverage the unique characteristics of AI workloads to create value that is not available in conventional electricity-consuming facilities.

11.1 Renewable Forecasting and Uncertainty

Accurate forecasting of renewable energy supplies is the key to implementing effective demand-side management. The accuracy of solar forecasting depends on the time scale forecasted (3–12% MAPE for day-ahead forecasts using numerical weather prediction models; 3–8% MAPE for intra-hour forecasts based on satellite observations and sky-camera networks; and less than 3% MAPE for very short-term forecasting on the minute scale, according to persistence assumptions). Weather forecasting for wind is not as precise as solar forecasting, with day-ahead MAPE for renewables ranging from 10% to 18% based on a geographic area and terrain complexity. Machine learning post-processing based on LSTM and more sophisticated graph-based architectures has been shown to reduce MAPE by 20-30% from NWP raw data, especially at lead times between 1 and 6 hours[137].

Uncertainty also flows through the dispatch optimization process, and the control system must have reserves to accommodate forecast errors. Non-conservative dispatch strategies, such as planning for an optimistic energy supply, can lead to sub-optimal economic results but maintain reliability. Stochastic optimization methods explicitly capture the uncertainty in the forecasting process by incorporating probability distributions into the optimization, offering a more delicate trade-off between economic efficiency and reliability. Considering the uncertainty in forecasting and increased grid volatility, the framework suggests maintaining a minimum reserve margin of 15–20% above the forecast of renewable shortfall [177].

11.2 AI Workload Scheduling and Load Shifting

AI workload scheduling is the first paradigm shift in the DSG and takes advantage of the flexibility of many workloads to schedule them to coincide with the availability of green electricity. Training workloads, which are the most power-intensive but also the most flexible, can be deferred by hours to days without impacting project timelines, as long as the total compute time budgets are maintained[170]. For example, a frontier model with a training energy of 10,000-50,000 MWh can, in theory, be spread over a longer training duration to ramp down the peak power consumption if the training algorithm can be checkpointed and resumed later.

Latency requirements make the scheduling challenge for inference workloads more complicated. The interaction with users depends on sub-100ms response times and must not be postponed, as in real-time inference, the user will be waiting for a response to the action. Batch inference (including image processing, document processing, or model scoring) can be flexed for minutes to hours and is suitable for load shifting. A tiered scheduling approach — prioritizing real-time inference, then batch inference, then training workloads, then background tasks — provides a systematic method for allocating limited renewable energy across competing compute demands.

The EMS maintains a renewable availability API that provides 24–48-hour forecasts that indicate the portion of the workload that can be achieved without depending on non-renewable resources. The scheduler will ask this API for the period of the day when there is excess renewable generation to schedule lower priority workloads. Cost incentive measures, such as internal carbon pricing and shadow electricity prices based on the marginal cost of renewable energy, offer economic signals for application teams to optimize energy efficiency and align with renewable energy resources.

11.3 Multi-Facility Load Balancing and Geographic Diversity

Multi-facility loads balancing exploits the spatial variability of renewable resources across geographically distributed data centers. Facilities separated by more than 500 km typically exhibit low correlation in wind and solar generation, enabling the load to be routed to facilities with the most favorable current renewable conditions. A practical example: an operator with facilities on the U.S. East Coast and West Coast can exploit the three-hour time zone difference and different weather patterns to shift workloads, potentially reducing aggregate storage requirements by 50% to 70%.

Technical constraints on multi-facility workload balancing primarily involve network latency, as certain workloads cannot tolerate inter-region delays; data residency requirements, where regulations like GDPR mandate processing within specific geographic borders; and inter-facility data transfer costs, which typically range from $5 to $15 per Mbps per month for dedicated connections. Conversely, optimal workload pools for geographic distribution include stateless inference workloads that are easily replicated across regions, batch processing with minimal real-time networking dependencies, and proactively replicated datasets that mitigate large data transfer overheads during workload migration.

11.4 Real-Time Demand Response and Grid Services

Data center battery systems and flex load applications can benefit from programs in wholesale electricity markets that provide revenue and contribute to grid reliability. The planned introduction of primary frequency response (PFR) will see the data center power consumption or battery discharge automatically change within seconds of detecting any frequency deviation, thereby creating a new grid stability service previously provided by synchronous generators[171].

Based on market data of approximately $100 per MW per hour (4,000 hours of annual supply) for a 100 MW data center with 10 MW of PFR capacity for backup, that power source can generate approximately $4 million in revenue annually.  Voltage support services, which provide reactive power (VARs) to maintain voltage levels in the distribution system, represent another revenue opportunity. Grid-forming and voltage-source control (VSC) inverters can supply reactive power while having no impact on real power generation, thereby allowing them to be used for zero-marginal-cost ancillary services. The economic valuation of an inverter capacity of a 100 MW data center shows that the savings generated per year from voltage support services in a data center range from USD 750,000 to USD 1.5 million based on the market value and locational incremental value[172].

11.5 Energy Management System and Control Architecture

Here, the EMS uses a hierarchical control system architecture with three timescales and varying control objectives. Level 1 (device-level) reacts to changes in frequency and voltage in milliseconds to deliver the primary frequency response and voltage regulation via the inverter/battery controller. With 24-to-48-hour horizons and model predictive control, Level 2 (facility-level) implements dispatch optimization hours, achieving a balance of minimizing energy cost/and or carbon emissions while maintaining reliability targets. Level 3 (corporate level) is responsible for the allocation of resources across multiple facilities, routing workloads to facilities whose renewable conditions are most favorable and coordinating inter-facility energy exchanges. The EMS's capabilities encompass forecasting, optimization, monitoring, and cyber security. Forecast modules include solar, wind, and load forecasts over a range of time scales. Optimization modules formulate and solve the dispatch problem as a mixed-integer linear program (MILP) or use heuristic algorithms for real-time decision-making. Data collection modules gather information from metering points around the site and deliver dashboards, trending, alarms, and automated reporting[144].

# 12. Regulatory, Policy, and Sustainability

This section examines the regulatory environment, policy frameworks, and sustainability standards that govern the design and operation of renewable-powered data centers. Effective navigation of this landscape is essential for project permitting, interconnection, and long-term compliance with evolving environmental requirements of the industry.

12.1 Grid Interconnection Standards

Grid Interconnection Standards are technology and operational criteria that distributed energy resources must abide by getting connected to the main power grid. Up to now, the basis of distribution-level interconnections is IEEE 1547. On the data center scale, which typically involves medium-voltage or transmission-voltage installation with generation capacity ranging from 10 to 100 MW, the relevant standards that apply are IEEE 2800-2022 and Inverter-based resources (IBRs) [173]. IBRs deployed in low-system-strength zones will soon become increasingly common in data centers, where the short circuit ratio (SCR) becomes an important measurement of grid stability to guarantee the stability of control[130], [174]. In today's interconnection studies, IBR fault ride-through and dynamic voltage support during transients are given significant attention. FERC Order 2023 (issued July 2023, with implementation ongoing through 2027) represented a major reform of transmission interconnection procedures by shifting to cluster studies and penalizing study delays. However, its implementation across regional transmission operators (RTOs) remains an ongoing challenge; as of the end of 2025, over 2,060 GW of generation and storage capacity was actively stalled in interconnection queues[175].

12.2 Renewable Energy Policies and Mandates

Renewable Portfolio Standards (RPS) and Clean Energy Standards (CES) require utilities to buy a percentage of electricity from renewables. State-level calls for corporate renewable procurement persist in the United States. However, as AI workloads continue to ramp up at an unprecedented rate, they have rapidly accelerated the shift in procurement moves, projecting up to 945 TWh yearly worldwide by 2030[176]. In response to this demand, leading data center companies are turning to nuclear generation partnership arrangements alongside traditional wind and solar PPAs to obtain baseload zero-carbon electricity. The EU Renewable Energy Directive (RED III) lays out a legal 42.5% RE target in Europe until 2030. This legislation (reported requirements) is now functioning as a catalyst for the creation of direct corporate PPAs and clean generation schemes[177].

12.3 Carbon Accounting and Environmental Reporting

The standard framework for corporate carbon accounting is the Greenhouse Gas (GHG) Protocol. Scope 2 emissions include those arising from purchased electricity, using either location-based or market-based accounting methods. The transition to 24/7 carbon-free Energy (CFE) – pairing every hour of electricity usage with carbon-free electricity generation – has proven to be the new benchmark for data center sustainability. Implementing 24/7 CFE requires sub-hourly granular data, advanced forecasting, and stringent temporal and spatial carbon accounting frameworks to verify continuous clean energy alignment and prevent the double-counting of clean energy attributes[111].

12.4 Environmental Impact Assessment

The environmental footprint of renewable energy projects and data centers with artificial intelligence needs to be minimized. Cooling systems for data centers offer a clear choice between electric-powered air cooling and water-powered evaporative cooling. Before the AI revolution, data centers in the U.S. alone consumed an estimated 17.4 billion gallons of water per year as of 2014, a figure that has grown substantially with AI infrastructure buildout[2], and as demand for hyperscale facilities grows, it is estimated that their water consumption will scale up substantially. By 2030, the water consumption generated by global AI activity could exceed the minimum annual requirement for each person's domestic needs by 1.3 billion people, while biodiversity and land use effects vary by site. Moreover, the short lifespan, which tech giants favor in their AI hardware, is leading to an electronic waste problem: by 2030, the total amount of AI infrastructure expected to contribute to e-waste is up to 2.5M tons each year [176].

12.5 Regulatory Barriers and Opportunities

Interconnection queue congestion is a major regulatory barrier for renewable-powered data centers today. In the past decade, the number of requests has grown substantially, and 2500 to 3,000 new requests have been submitted for new interconnection capacity of 400-750 GW/year. This has left a significant backlog, which is delaying efforts to integrate clean energy. Other hurdles involving distributed generation include distribution system design barriers (one-way power flow, no bidirectional), permitting barriers (environmental review, building permits/approvals, utility coordination), and opposition from incumbent utilities.  Alternative routes exist, such as community choice aggregation (CCA) and green tariff programs, and interconnection complexity and costs can be mitigated with behind-the-meter exemptions. Policy recommendations based on the framework analysis are (1) streamline interconnection following the FERC Order 2023 format, including practices such as the U.S. Department of Energy's i2X roadmap to automate data collection and standardize cluster study parameters; (2) continue and increase renewable energy tax credits (ITC and PTC) to provide grid investment certainty; (3) clarify and update zoning and building code requirements to support on-site renewable generation and storage; (4) ensure grid data centers are viable through an aggressive research program in the area of 24/7 CFE accounting methodology, establishing a transparent, standardized approach to 24/7 CFE accounting for the stability of IBRs operating on weak grids; and (5) support grid modernization research with a focus on the stability of IBRs (Inverter-Based Resources) on weak grids to achieve data center reliability[174], [178].

12.6 Sustainability Certifications and Reporting

Voluntary sustainability certifications are rapidly becoming regulatory compliance frameworks. Approximately 50,000 companies are subject to the European Union's Corporate Sustainability Reporting Directive (CSRD), which has introduced uniform reporting standards for Environmental, Social, and Governance (ESG) metrics. At the same time, the International Sustainability Standards Board (ISSB) has developed a global foundation for sustainability finance disclosures that has changed corporate accountability in S1 and S2 IFRS Sustainability-related financial disclosures.  As a result, multinational data center operators now need to gather and cross-validate granular data points across all their operational footprints and supply chains. Concerns regarding the digital industry's increasing environmental footprint have resulted in a comprehensive framework of EU laws and policy that seeks to build climate-neutral and energy-efficient data centers by 2030. LEGACY Standards, such as LEED and ISO 50001 and the Uptime Institute's Tier Standard, are still significant benchmarks to use during operation, but are increasingly being incorporated into these higher-level compliance frameworks[170], [179].

# 13. Conclusions

This review presents a seven-component framework for designing, deploying, and operating AI data centers powered by renewable energy. The framework integrates site assessment and resource evaluation, technology mix optimization, electrical architecture design, hierarchical control and dispatch strategies, demand-side workload flexibility, economic viability modeling, and sustainability and resilience compliance into a single unified methodology. This framework connects engineering, operational, financial, and regulatory considerations, whereas prior research primarily addressed either technical performance or economic feasibility in isolation. By placing renewable generation, energy storage, grid connection, and workload scheduling within one analytical structure, this framework provides a scalable, deployable path to reliable and cost-effective clean energy for AI computing infrastructure.

13.1 Key Technical Findings

The cost trajectories of renewable energy and storage technologies are firmly established. Since 2010, solar PV installed costs have dropped by more than 90%, with current utility-scale prices in the range of $0.70 to $1.20/W depending on project scale and geography. Wind and solar generation profiles exhibit strong seasonal complementarity, improving system reliability while reducing storage requirements. Geographic diversification and hybrid renewable portfolios can reduce battery storage requirements by approximately 40–60% compared to single-technology solar-only deployments. Lithium iron phosphate (LFP) battery systems remain the dominant short-to-medium duration storage technology for data center applications. Pack-level costs have fallen to approximately $108/kWh in 2025 and are projected to decline further to $65–95/kWh by 2030, making renewable-powered operations increasingly economically viable. The results demonstrate that hybrid renewable energy systems with 4–8 h of battery storage can meet 99.9% reliability targets while achieving an LCOE of $35–80/MWh, placing them at or below the cost of grid-supplied electricity in high-demand markets.

13.2 Key Economic Findings

The economic analysis demonstrates that renewable-powered AI data centers can yield strong financial returns under current market conditions. Through federal incentive programs such as the Investment Tax Credit under the Inflation Reduction Act and its associated bonus provisions, capital cost reductions are sufficient to achieve simple payback periods of 4–8 years for many projects. Net present value analysis indicates values of approximately $30 million to $120 million for a representative 100 MW facility, depending on local electricity costs, renewable resource quality, financing assumptions, and storage system costs. Comparative cost analysis further indicates that hybrid renewable systems can achieve a benchmark LCOE of approximately $55/MWh, substantially below the equivalent cost of $110/MWh for conventional grid-dependent operations in high-demand AI computing infrastructure.

13.3 Implementation Recommendations

For mid-scale operators (10–100 MW), probabilistic storage sizing approaches, such as loss-of-load expectation (LOLE), are recommended over deterministic worst-case approaches. These methodologies typically yield capital expenditure savings of 30–60% in the storage infrastructure while maintaining equivalent reliability performance. For hyperscale facilities exceeding 100 MW, geographic load balancing and multi-regional energy procurement should be incorporated at the planning stage. Operators using distributed renewable portfolios and coordinated workload allocation may reduce per-facility storage requirements by 50–70% while improving overall system resilience. Across all facility scales, early engagement with transmission operators and utility interconnection processes is critical. As interconnection queues in many regions extend for several years, project developers should initiate interconnection applications at least two years before the expected construction start date to mitigate deployment delays and associated financial risks.

# 14. Future Research Directions and Emerging Technologies

This section identifies unresolved research questions and next-generation technologies that will shape the evolution of renewable-powered data centers in the coming decade and beyond. The analysis distinguishes between near-term opportunities (1–5 years), medium-term developments (5–10 years), and long-term transformations (10+ years).

14.1 Next-Generation Computing Paradigms

Although quantum computing is not necessarily meant to out-compete classical GPUs in the AI training and inference space, it does come with its own set of energy demands. Current quantum processors are cryogenically cooled to near-absolute-zero (10-20 millikelvin) and require 1-10 kW of cooling for every 10 qubits[170]. The overall energy impact of the data center will be small; however, quantum operations require very stable power generation to avoid state decoherence.

Neuromorphic computing relies on spiking neural networks to replicate biological neural computation and could yield order-of-magnitude energy savings. Implementations of 'neuromorphic' architectures have shown as much as 100 times greater energy efficiency than state-of-the-art GPUs for certain pattern recognition applications that are event driven[180]. Yet, a less-developed software ecosystem and the inability of dominant models based on transformers to support the DGX ecosystem of neuromorphic training approaches have stood as an obstacle to widespread adoption.

Photonic (optical) computing and interconnects represent the most imminent paradigm shift for AI energy reduction. An increasing number of photonic interconnects are available commercially and help to solve the serious power constraint problem of copper wiring for GPU clusters by scaling down the energy per bit needed for data communication by one order of magnitude. In addition, analogue optical computing processors have demonstrated a level of inference that is greater than 160 TOPS/W (trillion operations per second per watt) in laboratories[181].

14.2 Advanced Energy Storage Technologies

A near-term possible improvement for high-density, low-footprint energy storage is solid-state and lithium-metal batteries, which promise 2–3 times the energy density of today's lithium-ion batteries. Commercialization for stationary storage applications is now moving rapidly, and stationary pricing is expected to reach parity with LFP chemistries by the end of the decade[182].

Form Energy's iron air battery technology moved from pilot projects to gigawatt-scale commercial production in 2026, which is critical for 24/7 carbon-free energy matching. Iron-air deployments are designed for multi-day storage time and a considerably lower cost than lithium-ion batteries, constituting a paradigm shift for data center that must span multi-day renewable energy deficits[114]. A low-carbon hydrogen source can provide seasonal storage times. Now, costs need to drop dramatically, from $2/kg to less than $1/kg, for economic viability in data center backup applications—a long-term target of massive amounts of electrolyze scale-up and reductions in renewable electricity cost.

14.3 AI and Machine Learning for Grid Optimization

Machine learning is being applied in many ways across the grid, be it forecasting, real-time dispatch, or predictive maintenance. Technologies such as spatio-temporal networks and transformer-based time-series models have been shown to boost the accuracy of solar and wind forecasts by 20–30% compared to traditional numerical weather prediction models[114]. Reinforcement learning (RL) agents are known to be highly effective in learning optimal policies for multi-microgrid dispatch, consistently outperforming conventional rule-based or purely deterministic approaches in complex multi-objective optimization problems, while continuously interacting with simulated environments. Additionally, systems for predictive maintenance with applications based on anomaly detection algorithms on the edge can detect trends in insulation and mechanical degradation of equipment in substations at an early stage. This is proactive maintenance (before catastrophic fault) that can be scheduled and minimize unplanned downtime in the facility. Developing autonomous grid control with AI is challenging because of the lack of ability to generalize the models and provide guarantees over the training distribution, especially for high-impact, low-frequency extreme weather events[183].

14.4 Challenges for a 100 percent Renewable Grid

The structural stability challenges faced by power systems operating with a renewable penetration of more than 80% are qualitatively different from those faced by power systems operating in a traditional manner. Conventional thermal generation has been retired, leaving frequency nadir and rate of change of frequency (RoCoF) dynamics as a significant challenge. In this operating environment, fast acting Inverter Based Resources (IBRs) with Grid-Forming Control (GFC) is required to provide synthetic inertia and help stabilize sub-second frequency deviations [184].

Moreover, weak grid conditions, such as low system strength and low short circuit ratios (SCR), pose serious risks of control interaction and transient voltage instability when operating the equipment. With a growing number of deep generation oversupply and deep generation undersupply events, the system needs to be highly coordinated from the millisecond level of dynamic voltage support to seasonal energy storage dispatch[173].

Unlike conventional loads, data centers can be used to stabilize low-inertia grids. They can run as "anchor loads" and help ensure financial certainty for new clean energy projects. At the same time, data centers can use their on-site battery energy storage systems (BESS) and flexible computing architectures to provide the balancing authority with much-needed frequency response (FR), primary frequency response (PFR), and automated demand response (ADR) services at speeds that can be as rapid as a few seconds or as instantaneous as a few milliseconds[109].

14.5 Integration with Grid Modernization

Smart grid technologies, including advanced distribution automation, localized microgrid designs, and power bidirectionality, are creating fertile ground for deep data center integration. Optimized vehicle-to-grid (V2G) multi-facility aggregation could decrease a data center 's stationary battery footprint by 30–50% by using co-located vehicle fleet infrastructure facilities as a single energy buffer. Another obvious optimization path is thermal modernization. Hyperscale facilities are quickly moving to liquid cooling loops to support high-density AI clusters and are rejecting high-grade waste heat, often in excess of 60°C. This increased temperature resource enables very effective integration with nearby municipal district heating or district cooling systems and/or adjacent industrial processes, resulting in a significant reduction in the comprehensive power usage effectiveness (PUE) and total resource effectiveness (TRE) of the facility[185].

14.6 Recommendations for Future Research

- Near-Term Goals (1 to 5 Years): Implement sub-hour 24/7 CFE tracking protocols in a standard way (using cryptographic granular certificates); utilize the stability of the control loop in the grid-forming inverter (GFI) under low SCR conditions to validate the stability of the control loop within data center (DC) microgrids; and field-test AI-based workload shifting in correlation with local distribution constraint signals.

- Medium-Term Priorities (5 to 10 years): Assess the ways in which LDES and LLAES assets can be scaled up for use in a seasonal manner for data center backup; determine the lifecycle degradation of LDES and LLAES assets when they are scaled up; identify multiple-party co-optimization algorithms for cross-sector thermal coupling between liquid-cooled data centers and district utility networks; and characterize wide-area coordination challenges of multi-gigawatt data center clusters operating in 100 percent inverted-dominated grids.

- Medium-to long-term priorities (10+ years): Demonstrate the operational scalability of analogue optical and neuromorphic computing concepts for handling full production workloads for supporting AI training; validate the economic and logistical feasibility of large-scale green hydrogen ecosystems for providing multi-week, seasonal backup power using zero-emission energy; and develop plug-and-play standards for fully decentralised, self-healing autonomous microgrids operating in island mode.

References

[1]	IEA, “Data Centers and Data Transmission Networks.” [Online]. Available: https://www.iea.org/energy-system/buildings/data-centers-and-data-transmission-networks

[2]	A. Shehabi et al., “United States Data Center Energy Usage Report,” LBNL--1005775, 1372902, Jun. 2016. doi: 10.2172/1372902.

[3]	IEA, “Energy and AI.” Accessed: Apr. 10, 2025. [Online]. Available: https://www.iea.org/reports/energy-and-ai

[4]	D. Patterson et al., “Carbon Emissions and Large Neural Network Training,” 2021, arXiv. doi: 10.48550/ARXIV.2104.10350.

[5]	E. Strubell, A. Ganesh, and A. McCallum, “Energy and Policy Considerations for Deep Learning in NLP,” 2019, arXiv. doi: 10.48550/ARXIV.1906.02243.

[6]	F. Jeanquartier et al., “Assessing the carbon footprint of language models: Towards sustainability in AI,” Resour. Conserv. Recycl., vol. 226, p. 108670, Feb. 2026, doi: 10.1016/j.resconrec.2025.108670.

[7]	J. Shi, Z. Yang, and D. Lo, “Efficient and Green Large Language Models for Software Engineering: Literature Review, Vision, and the Road Ahead,” Dec. 04, 2024, arXiv: arXiv:2404.04566. doi: 10.48550/arXiv.2404.04566.

[8]	X. Chen, X. Wang, A. Colacelli, M. Lee, and L. Xie, “Electricity Demand and Grid Impacts of AI Data Centers: Challenges and Prospects,” Nov. 26, 2025, arXiv: arXiv:2509.07218. doi: 10.48550/arXiv.2509.07218.

[9]	D. Donnellan et al., “Uptime Institute Global Data Center Survey 2024,” 2024, [Online]. Available: https://uptimeinstitute.com/resources/research-and-reports/uptime-institute-global-data-center-survey-results-2024

[10]	M. Andersch et al., “NVIDIA Hopper Architecture In-Depth”, [Online]. Available: https://developer.nvidia.com/blog/nvidia-hopper-architecture-in-depth/

[11]	K. Calvin et al., “IPCC, 2023: Climate Change 2023: Synthesis Report. Contribution of Working Groups I, II and III to the Sixth Assessment Report of the Intergovernmental Panel on Climate Change [Core Writing Team, H. Lee and J. Romero (eds.)]. IPCC, Geneva, Switzerland.,” Intergovernmental Panel on Climate Change (IPCC), Jul. 2023. doi: 10.59327/IPCC/AR6-9789291691647.

[12]	“Driving sustainable innovation for society.” [Online]. Available: https://datacenters.google/operating-sustainably/

[13]	D. Feldman et al., “Spring 2024 Solar Industry Update,” NREL/PR--7A40-90042, 2376145, MainId:91820, May 2024. doi: 10.2172/2376145.

[14]	IRENA, “Renewable power generation costs in 2023”, [Online]. Available: https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2024/Sep/IRENA_Renewable_power_generation_costs_in_2023.pdf

[15]	IEA, “Wind.” Accessed: Feb. 25, 2025. [Online]. Available: https://www.iea.org/energy-system/renewables/wind

[16]	“Renewable power generation costs in 2024”, [Online]. Available: https://www.rinnovabili.it/wp-content/uploads/2025/07/IRENA-RENEWABLE-POWER-GENERATION-COSTS-IN-2024.pdf

[17]	BNEF, “BNEF: Lithium-ion battery pack prices fall to $108/kWh, stationary storage becomes lowest price segment.” Accessed: Dec. 09, 2025. [Online]. Available: https://www.ess-news.com/2025/12/09/bnef-lithium-ion-battery-pack-prices-fall-to-108-kwh-stationary-storage-becomes-lowest-price-segment/

[18]	G. Song, B. Cao, and L. Chang, “Review of Grid-forming Inverters in Support of Power System Operation,” Chin. J. Electr. Eng., vol. 8, no. 1, pp. 1–15, Mar. 2022, doi: 10.23919/CJEE.2022.000001.

[19]	G. Rostirolla et al., “A survey of challenges and solutions for the integration of renewable energy in datacenters,” Renew. Sustain. Energy Rev., vol. 155, p. 111787, Mar. 2022, doi: 10.1016/j.rser.2021.111787.

[20]	D. Harrison-Atlas, C. Murphy, A. Schleifer, and N. Grue, “Temporal complementarity and value of wind-PV hybrid systems across the United States,” Renew. Energy, vol. 201, pp. 111–123, Dec. 2022, doi: 10.1016/j.renene.2022.10.060.

[21]	C. Wu, X.-P. Zhang, and M. Sterling, “Solar power generation intermittency and aggregation,” Sci. Rep., vol. 12, no. 1, p. 1363, Jan. 2022, doi: 10.1038/s41598-022-05247-2.

[22]	IEEE Standard for Harmonic Control in Electric Power Systems. doi: 10.1109/IEEESTD.2022.9848440.

[23]	M. C. Offutt and L. Zhu, “Data Centers and Their Energy Consumption: Frequently Asked Questions”.

[24]	“Improvements to Generator Interconnection Procedures and Agreements.” Accessed: Sep. 06, 2023. [Online]. Available: https://www.federalregister.gov/documents/2023/09/06/2023-16628/improvements-to-generator-interconnection-procedures-and-agreements

[25]	S. Cai and Z. Gou, “Towards energy-efficient data centers: A comprehensive review of passive and active cooling strategies,” Energy Built Environ., vol. 7, no. 1, pp. 206–226, Feb. 2026, doi: 10.1016/j.enbenv.2024.08.009.

[26]	R. Mural et al., “AI, Data Centers, and the U.S. Electric Grid: A Watershed Moment”, [Online]. Available: https://www.belfercenter.org/research-analysis/ai-data-centers-us-electric-grid

[27]	C. Zhao, W. Gao, F. Nie, and H. Zhou, “A Survey of GPU Multitasking Methods Supported by Hardware Architecture,” IEEE Trans. Parallel Distrib. Syst., vol. 33, no. 6, pp. 1451–1463, Jun. 2022, doi: 10.1109/TPDS.2021.3115630.

[28]	V. Avelar and P. Donovan, “How 6 AI Attributes Change Data Center Design”, [Online]. Available: https://download.schneider-electric.com/files?p_Doc_Ref=SPD_WP110_EN&p_enDocType=White+Paper&p_File_Name=WP110_V3_1_EN.pdf

[29]	T. B. Brown et al., “Language Models are Few-Shot Learners,” 2020, arXiv. doi: 10.48550/ARXIV.2005.14165.

[30]	M. Raza, “Carbon Literacy for Generative AI: Visualizing Training Emissions Through Human-Scale Equivalents”, [Online]. Available: https://openreview.net/forum?id=86NT1eVitH&referrer=%5Bthe%20profile%20of%20Mahveen%20Raza%5D(%2Fprofile%3Fid%3D~Mahveen_Raza1)

[31]	Google, “Growing the internet while reducing energy consumption.” [Online]. Available: https://datacenters.google/efficiency/

[32]	D. Al Kez, A. M. Foley, F. W. B. M. Hasan Wong, A. Dolfi, and G. Srinivasan, “AI-driven cooling technologies for high-performance data centers: state-of-the-art review and future directions,” Sustain. Energy Technol. Assess., vol. 82, p. 104511, Oct. 2025, doi: 10.1016/j.seta.2025.104511.

[33]	X. Zhang, T. Lindberg, N. Xiong, V. Vyatkin, and A. Mousavi, “Cooling Energy Consumption Investigation of Data Center IT Room with Vertical Placed Server,” Energy Procedia, vol. 105, pp. 2047–2052, May 2017, doi: 10.1016/j.egypro.2017.03.581.

[34]	M. Azarifar, M. Arik, and J.-Y. Chang, “Liquid cooling of data centers: A necessity facing challenges,” Appl. Therm. Eng., vol. 247, p. 123112, Jun. 2024, doi: 10.1016/j.applthermaleng.2024.123112.

[35]	D. Zhou et al., “Accelerating liquid cooling adoption in data centers: necessity, challenges and solutions,” Technol. Rev. Carbon Neutrality, p. 9550014, Dec. 2025, doi: 10.26599/TRCN.2025.9550014.

[36]	J. Hurni et al., “Over 31%-efficient perovskite–TOPCon solar cells enabled by AlO x  -based hydrogenation and front sub-micron texturing,” EES Sol., vol. 1, no. 5, pp. 732–735, 2025, doi: 10.1039/D5EL00105F.

[37]	G. Galioto, G. Vitale, A. Sferlazza, G. Lullo, and G. C. Giaconia, “Wide and Ultrawide Bandgap Power Semiconductors: A Comprehensive System-Level Review,” Electronics, vol. 15, no. 4, p. 835, Feb. 2026, doi: 10.3390/electronics15040835.

[38]	P. Blecich, I. Bonefačić, T. Senčić, and I. Wolf, “Resilience Under Heatwaves: Croatia’s Power System During the July 2024 Heatwave and the Role of Variable Renewable Energy by 2030,” Appl. Sci., vol. 15, no. 12, p. 6440, Jun. 2025, doi: 10.3390/app15126440.

[39]	G. Gülen, J. Das, and M. H. Young, “Assessing Economic Costs of Two Reliable Generation Mix Scenarios in the ERCOT System,” Energies, vol. 19, no. 9, p. 2195, May 2026, doi: 10.3390/en19092195.

[40]	A. McCoy et al., “Offshore Wind Market Report: 2024 Edition”, [Online]. Available: https://docs.nlr.gov/docs/fy24osti/90897.pdf

[41]	N. Lukač, G. Štumberger, and B. Žalik, “Wind resource assessment using airborne LiDAR data and smoothed particle hydrodynamics,” Environ. Model. Softw., vol. 95, pp. 1–12, Sep. 2017, doi: 10.1016/j.envsoft.2017.05.006.

[42]	E. Virguez et al., “Renewable energy quality trilemma and coincident wind and solar droughts”, doi: 10.17615/C4JD-4Y42.

[43]	M. Bošnjaković, N. Veljić, J. T. Božič, and S. Muhič, “SWOT-AHP Analysis of the Importance and Adoption of Pumped-Storage Hydropower,” Technologies, vol. 13, no. 7, p. 305, Jul. 2025, doi: 10.3390/technologies13070305.

[44]	M. Catania, F. Parolin, F. Fattori, and P. Colbertaldo, “The role of hydropower in decarbonisation scenarios,” Renew. Energy, vol. 236, p. 121411, Dec. 2024, doi: 10.1016/j.renene.2024.121411.

[45]	S. Evro, A. Ajumobi, D. Mayon, and O. S. Tomomewo, “Navigating battery choices: A comparative study of lithium iron phosphate and nickel manganese cobalt battery technologies,” Future Batter., vol. 4, p. 100007, Dec. 2024, doi: 10.1016/j.fub.2024.100007.

[46]	K. Chandra Bhowmik, Md. A. Rahman, Md. M. Billah, and A. Paul, “From Lithium‐Ion to Sodium‐Ion Batteries for Sustainable Energy Storage: A Comprehensive Review on Recent Research Advancements and Perspectives,” Chem. Rec., vol. 24, no. 12, p. e202400176, Dec. 2024, doi: 10.1002/tcr.202400176.

[47]	A. Barzigar, E. Ebadati, A. S. Mujumdar, and S. M. Hosseinalipour, “A comprehensive review of vanadium redox flow batteries: Principles, benefits, and applications,” Res., vol. 2, no. 4, p. 100767, Dec. 2025, doi: 10.1016/j.nexres.2025.100767.

[48]	European Commission. Joint Research Center et al., Clean Energy Technology Observatory. in EUR. LU: Publications Office of the European Union, 2026. doi: 10.2760/2686206.

[49]	U. Remme, “Global Hydrogen Review 2025,” 2025, [Online]. Available: https://iea.blob.core.windows.net/assets/12d92ecc-e960-40f3-aff5-b2de6690ab6b/GlobalHydrogenReview2025.pdf

[50]	T. Jaradat and T. Khatib, “A review of battery energy storage system for renewable energy penetration in electrical power system: Environmental impact, sizing methods, market features, and policy frameworks,” Future Batter., vol. 7, p. 100106, Sep. 2025, doi: 10.1016/j.fub.2025.100106.

[51]	M. M. Rana, H. Mo, G. M. Shafiullah, L. Qiao, and D. Dong, “Optimal sizing of battery storage for cost-effective peak shaving in regional distribution networks,” J. Energy Storage, vol. 141, p. 119502, Jan. 2026, doi: 10.1016/j.est.2025.119502.

[52]	Z. Ma, “From Grid-Following to Grid-Forming: A Review of Converter Technology Paradigm Shift and Its Applications in Renewable-Rich Power Systems,” Adv. Eng. Res. Possibilities Chall., vol. 2, no. 2, p. 37, Aug. 2025, doi: 10.63313/AERpc.9047.

[53]	IEEE Standard for Interconnection and Interoperability of Inverter-Based Resources (IBRs) Interconnecting with Associated Transmission Electric Power Systems. doi: 10.1109/IEEESTD.2022.9762253.

[54]	S. Shelar, D. Bankar, and S. Bakre, “Review of revisions of IEEE 519 Standard on Power System Harmonics (1981 to 2022),” in 2024 21st International Conference on Harmonics and Quality of Power (ICHQP), Chengdu, China: IEEE, Oct. 2024, pp. 415–420. doi: 10.1109/ICHQP61174.2024.10768696.

[55]	Google, “Google Environmental Report 2025.” [Online]. Available: https://sustainability.google/reports/google-2025-environmental-report/

[56]	O. A. Mavisclara et al., “The AI-Driven Energy Surge: A comprehensive review of sustainable power solutions for data centers,” Glob. J. Eng. Technol. Adv., vol. 24, no. 3, pp. 328–344, Sep. 2025, doi: 10.30574/gjeta.2025.24.3.0279.

[57]	Meta, “2025 Sustainability Report.” [Online]. Available: https://sustainability.atmeta.com/wp-content/uploads/2025/08/Meta_2025-Sustainability-Report.pdf

[58]	BloombergNEF, “Corporate Clean Energy Buying Fell in 2025 After Nearly a Decade of Growth.”

[59]	Y. Panchal, S. Dubey, and R. Pathak, “Exploring the Future of Cloud Computing: A Comprehensive Study of Microsoft’s Underwater Data Centers,” vol. 12, no. 3, 2025.

[60]	K. Simon, “Project Natick — Microsoft’s Self-sufficient Underwater Datacenters”, [Online]. Available: https://www.researchgate.net/publication/328214732_Project_Natick-Microsoft’s_Self-sufficient_Underwater_Datacenters

[61]	G. Gülen, J. Das, and M. H. Young, “Assessing Economic Costs of Two Reliable Generation Mix Scenarios in the ERCOT System,” Energies, vol. 19, no. 9, p. 2195, May 2026, doi: 10.3390/en19092195.

[62]	Equinix, “Sustainability Report 2025.” [Online]. Available: https://delivery-p112322-e1154416.adobeaemcloud.com/adobe/assets/deliver/urn:aaid:aem:116e6fc1-6217-4132-8fcf-1dc7096396df/Equinix-Inc_2025_Sustainability-Report.pdf

[63]	Apple, “Environmental Progress Report.” [Online]. Available: https://www.apple.com/environment/pdf/Apple_Environmental_Progress_Report_2025.pdf

[64]	IEEE Recommended Practice for the Design of Reliable Industrial and Commercial Power Systems (Gold Book). doi: 10.1109/IEEESTD.1998.89291.

[65]	I. Keskin and G. Soykan, “Reliability, availability, and life-cycle cost (LCC) analysis of combined cooling, heating and power (CCHP) integration to data centers considering electricity and cooling supplies,” Energy Convers. Manag., vol. 291, p. 117254, Sep. 2023, doi: 10.1016/j.enconman.2023.117254.

[66]	Nguyen Anh Huy and X. T. Nguyen, “Data center energy assessment process and energy efficiency metrics,” 2025, doi: 10.13140/RG.2.2.27710.75845.

[67]	J. Gavrila Mailuhu, M. A.F. Haurissa, and M. Jamlaay, “Design And Construction Of Automatic Transfer Switch (ATS) System With Backup Control System In Hybrid Power Plant (PLN - PLTS - GENSET),” Int. J. Sci. Technol. Manag., vol. 6, no. 3, pp. 520–527, Jun. 2025, doi: 10.46729/ijstm.v6i3.1316.

[68]	S. Narayanaswamy, P. D. Patel, I. Karlin, A. Gupta, S. Saripalli, and J. Guo, “Datacenter Energy Optimized Power Profiles,” 2025, arXiv. doi: 10.48550/ARXIV.2510.03872.

[69]	V. Singhania, S. Aga, and M. A. Ibrahim, “FinGraV: Methodology for Fine-Grain GPU Power Visibility and Insights,” Mar. 28, 2025, arXiv: arXiv:2412.12426. doi: 10.48550/arXiv.2412.12426.

[70]	Z. Yang, G. He, Y. Li, Y. Sun, W. Luo, and W. Zhang, “Thermal management in copackaged optics: from device assembly to system operation,” Adv. Photonics Nexus, vol. 5, no. 03, Mar. 2026, doi: 10.1117/1.APN.5.3.034001.

[71]	S. Mohammadi et al., “Grid Integration of AI Data Centers: A Critical Review of Energy Storage Solutions,” May 05, 2026, arXiv: arXiv:2603.00415. doi: 10.48550/arXiv.2603.00415.

[72]	Niranchana Radhakrishnan, “Optimizing Data Center Energy Efficiency with Dynamic Resource Allocation and Intelligent Cooling Management through Machine Learning,” J. Electr. Syst., vol. 20, no. 3s, pp. 286–293, Apr. 2024, doi: 10.52783/jes.1287.

[73]	T. W. A. Putra, N. D. Setiawan, and R. Rusito, “The Use of Machine Learning for Efficient Energy Management in Big Data-Based Computing Systems,” J. Technol. Inform. Eng., vol. 3, no. 3, pp. 324–336, Dec. 2024, doi: 10.51903/jtie.v3i3.202.

[74]	IEC, “Electrical Energy Storage.” [Online]. Available: https://iec.ch/system/files/2019-09/content/media/files/iec_wp-electrical_energy_storage-en.pdf

[75]	Y. Sheng et al., “Power for AI Data Centers: Energy Demand, Grid Impacts, Challenges and Perspectives,” Energies, vol. 19, no. 3, p. 722, Jan. 2026, doi: 10.3390/en19030722.

[76]	E. Eslami, “Air Quality and Greenhouse Gas Emissions Assessment of Data Centers in Texas: Quantifying Impacts and Environmental Tradeoffs,” 2025, arXiv. doi: 10.48550/ARXIV.2509.21312.

[77]	Y. Tang, X. Bai, C. Jin, Y. Fu, W. Mao, and X. Xu, “Experimental and numerical study on the thermal environment of a data center,” Build. Environ., vol. 212, p. 108741, Mar. 2022, doi: 10.1016/j.buildenv.2021.108741.

[78]	C. S. D. and S. Abimannan, “Energy Efficient Free Cooling System for Data Centers,” in 2011 IEEE Third International Conference on Cloud Computing Technology and Science, Athens, Greece: IEEE, Nov. 2011, pp. 646–651. doi: 10.1109/CloudCom.2011.100.

[79]	J. Yuan, Y. Yan, X. Zhang, X. Kong, and T. Zhang, “Coupling of flexible phase change materials and servers for improving the security of data centers in emergency situations,” Appl. Therm. Eng., vol. 242, p. 122439, Apr. 2024, doi: 10.1016/j.applthermaleng.2024.122439.

[80]	IEEE Recommended Practice for Powering and Grounding Electronic Equipment. doi: 10.1109/IEEESTD.1999.90559.

[81]	R. Siddique, “Active Power Filters for Harmonic Mitigation in Power Systems”.

[82]	A. Santos, G. Duggan, S. Frank, D. Gerber, and D. Zimmerle, “Endpoint Use Efficiency Comparison for AC and DC Power Distribution in Commercial Buildings,” Energies, vol. 14, no. 18, p. 5863, Sep. 2021, doi: 10.3390/en14185863.

[83]	A. F. Snyder and M. T. G. Stuber, “The ANSI C12 protocol suite - updated and now with network capabilities,” in 2007 Power Systems Conference: Advanced Metering, Protection, Control, Communication, and Distributed Resources, Clemson, SC, USA: IEEE, Mar. 2007, pp. 117–122. doi: 10.1109/PSAMP.2007.4740906.

[84]	J. Li, C. Wang, and Y. Liu, “AI Driven Virtual Power Plants: A Comprehensive Review,” Jan. 22, 2026, Engineering. doi: 10.20944/preprints202601.1691.v1.

[85]	S. Jadhav and Z. Liu, “Digital Twin-Based Cooling System Optimization for Data Center,” 2026, arXiv. doi: 10.48550/ARXIV.2603.01198.

[86]	NREL, “National Renewable Energy Laboratory (NREL).” [Online]. Available: https://atb.nrel.gov/

[87]	E. Förstner et al., “Photovoltaic system reduces grid voltage waveform distortions in the frequency range from 700 Hz to 1250 Hz,” 2026, doi: 10.5445/IR/1000191363.

[88]	L. Liu, H. Matayoshi, M. E. Lotfy, M. Datta, and T. Senjyu, “Load Frequency Control Using Demand Response and Storage Battery by Considering Renewable Energy Sources,” Energies, vol. 11, no. 12, p. 3412, Dec. 2018, doi: 10.3390/en11123412.

[89]	O. Ndindayino, A. Puel, and J. Meyers, “Effect of blockage on wind turbine power and wake development,” Feb. 12, 2025, Fluid mechanics/Wakes and wind farm aerodynamics. doi: 10.5194/wes-2025-6.

[90]	P. Toufani, E. C. Karakoyun, E. Nadar, O. B. Fosso, and A. S. Kocaman, “Optimization of pumped hydro energy storage systems under uncertainty: A review,” J. Energy Storage, vol. 73, p. 109306, Dec. 2023, doi: 10.1016/j.est.2023.109306.

[91]	J. F. S. De Paula, J. L. De Souza Silva, M. V. De Paula, G. Fraidenraich, and T. A. Dos Santos Barros, “A Two-Stage Methodology for Accurate PV Energy Yield Estimation Using Satellite Weather Data and PV Modeling Python Library,” in 2025 Brazilian Power Electronics Conference (COBEP), Vitoria, Brazil: IEEE, Oct. 2025, pp. 1–6. doi: 10.1109/COBEP66423.2025.11231587.

[92]	M. Ernst and J. Gooday, “Methodology for generating high time resolution typical meteorological year data for accurate photovoltaic energy yield modelling,” Sol. Energy, vol. 189, pp. 299–306, Sep. 2019, doi: 10.1016/j.solener.2019.07.069.

[93]	A. K. Nassar et al., “Multi-criteria GIS-based approach for optimal site selection of solar and wind energy,” Unconv. Resour., vol. 7, p. 100192, Jul. 2025, doi: 10.1016/j.uncres.2025.100192.

[94]	T. Anderson, “An improved typical meteorological year for solar energy simulations in Rarotonga, Cook Islands,” J. R. Soc. N. Z., vol. 52, no. 5, pp. 606–613, Oct. 2022, doi: 10.1080/03036758.2021.2013262.

[95]	C. Jung and D. Schindler, “Projections of energy yield- and complementarity-driven wind energy expansion scenarios in the European Union,” Energy Convers. Manag., vol. 269, p. 116160, Oct. 2022, doi: 10.1016/j.enconman.2022.116160.

[96]	NREL, “National Renewable Energy Laboratory (NREL). (2026).” [Online]. Available: https://atb.nrel.gov/

[97]	M. Li et al., “Renewable energy quality trilemma and coincident wind and solar droughts,” Commun. Earth Environ., vol. 5, no. 1, p. 661, Nov. 2024, doi: 10.1038/s43247-024-01850-5.

[98]	S. Jerez, I. Tobin, M. Turco, P. Jiménez-Guerrero, R. Vautard, and J. P. Montávez, “Future changes, or lack thereof, in the temporal variability of the combined wind-plus-solar power production in Europe,” Renew. Energy, vol. 139, pp. 251–260, Aug. 2019, doi: 10.1016/j.renene.2019.02.060.

[99]	X.-R. Zhu, J.-H. Tian, and Y. Wang, “The impact of climate change on wind and solar photovoltaic power potential and distribution in China,” Adv. Clim. Change Res., vol. 16, no. 4, pp. 730–746, Aug. 2025, doi: 10.1016/j.accre.2025.04.015.

[100]	W. Cole, V. Ramasamy, and M. Turan, “Cost Projections for Utility-Scale Battery Storage: 2025 Update,” Renew. Energy, 2025, [Online]. Available: https://docs.nrel.gov/docs/fy25osti/93281.pdf

[101]	Our World in Data, “Battery costs have declined by 99% in the last three decades, making electrified transport a reality.” [Online]. Available: https://ourworldindata.org/battery-price-decline

[102]	Y. Xie et al., “A high-fidelity online monitoring algorithm for multiple physical fields in battery pack,” Appl. Energy, vol. 398, p. 126443, Nov. 2025, doi: 10.1016/j.apenergy.2025.126443.

[103]	J. Vaičys, S. Gudžius, A. Jonaitis, R. Račkienė, A. Blinov, and D. Peftitsis, “A case study of optimising energy storage dispatch: Convex optimisation approach with degradation considerations,” J. Energy Storage, vol. 97, p. 112941, Sep. 2024, doi: 10.1016/j.est.2024.112941.

[104]	D. Reber, S. Jarvis, and M. Marshak, “The role of energy density for grid-scale batteries,” Nov. 17, 2022. doi: 10.26434/chemrxiv-2022-5ddhs.

[105]	S. Rahman and T. A. Khan, “Energy Storage Systems for AI Data Centers: A Review of Technologies, Characteristics, and Applicability,” Energies, vol. 19, no. 3, p. 634, Jan. 2026, doi: 10.3390/en19030634.

[106]	F. Yang, Z. Wang, and X. Tian, “Estimating future costs of hydrogen as long-duration energy storage based on a learning rate approach,” Clean Energy, vol. 10, no. 2, pp. 146–155, Mar. 2026, doi: 10.1093/ce/zkaf075.

[107]	X. Dong, Z. Yang, Q. Zhu, J. Li, B. Zhou, and J. Zhu, “Research on Reliability Evaluation Method of Distribution Network Considering the Temporal Characteristics of Distributed Power Sources,” Processes, vol. 14, no. 8, p. 1296, Apr. 2026, doi: 10.3390/pr14081296.

[108]	M. T. Takci, M. Qadrdan, J. Summers, and J. Gustafsson, “Data centers as a source of flexibility for power systems,” Energy Rep., vol. 13, pp. 3661–3671, Jun. 2025, doi: 10.1016/j.egyr.2025.03.020.

[109]	H. H. H. Mousa, K. Mahmoud, and M. Lehtonen, “Recent developments of demand‐side management towards flexible DER‐rich power systems: A systematic review,” IET Gener. Transm. Distrib., vol. 18, no. 13, pp. 2259–2300, Jul. 2024, doi: 10.1049/gtd2.13204.

[110]	EIA, “Electric Power Annual 2024.” [Online]. Available: https://www.eia.gov/electricity/annual/pdf/epa.pdf

[111]	Q. Xu, W. Ricks, A. Manocha, N. Patankar, and J. D. Jenkins, “System-level impacts of voluntary carbon-free electricity procurement strategies,” Joule, vol. 8, no. 2, pp. 374–400, Feb. 2024, doi: 10.1016/j.joule.2023.12.007.

[112]	Y. A. Sultan, S. S. Kaddah, and M. A. Elhosseini, “Enhancing smart grid transient performance using storage device‐based MPC controller,” IET Renew. Power Gener., vol. 11, no. 10, pp. 1316–1324, Aug. 2017, doi: 10.1049/iet-rpg.2016.0892.

[113]	Y. Hu, Z. Li, and J. Cui, “An economic model predictive control strategy for EV-integrated microgrids considering battery degradation,” Energy, vol. 335, p. 138205, Oct. 2025, doi: 10.1016/j.energy.2025.138205.

[114]	L. Friedel, J. Grenz, and C. Hagist, “A comparison of long duration energy storage technologies based on levelized cost of storage,” J. Energy Storage, vol. 153, p. 120679, Apr. 2026, doi: 10.1016/j.est.2026.120679.

[115]	J. M. Morales, A. J. Conejo, H. Madsen, P. Pinson, and M. Zugno, Integrating Renewables in Electricity Markets: Operational Problems, 1st ed. 2014. in International Series in Operations Research & Management Science, no. 205. New York, NY: Springer US : Imprint: Springer, 2014. doi: 10.1007/978-1-4614-9411-9.

[116]	J. Kim et al., “Reviewing the socio-technical dynamics of AI, data centers and digitalization on energy and the environment,” Renew. Sustain. Energy Rev., vol. 234, p. 116861, Jul. 2026, doi: 10.1016/j.rser.2026.116861.

[117]	Idaho National Lab, “Powering Data Centers with Clean Energy.” [Online]. Available: https://gain.inl.gov/content/uploads/4/2024/11/INL-RPT-24-79307-Powering-Data-Cneters-with-Clean-Energy.pdf

[118]	S. Babamohammadi, A. R. Birss, H. Pouran, J. Pandhal, and T. N. Borhani, “Emission control and carbon capture from diesel generators and engines: A decade-long perspective,” Carbon Capture Sci. Technol., vol. 14, p. 100379, Mar. 2025, doi: 10.1016/j.ccst.2025.100379.

[119]	S. Ghosh and J. Damodara, “Scalable data centers – Power generation and delivery challenges and solutions,” Energy Rep., vol. 15, p. 109178, Jun. 2026, doi: 10.1016/j.egyr.2026.109178.

[120]	EPRI, “Powering Data Centers in the AI Era.” [Online]. Available: https://energie.hec.ca/wp-content/uploads/2025/10/PPT_EPRI.pdf

[121]	J. W. Zhang, Y. H. Wang, G. C. Liu, and G. Z. Tian, “A review of control strategies for flywheel energy storage system and a case study witModelling converter,” Energy Rep., vol. 8, pp. 3948–3963, Nov. 2022, doi: 10.1016/j.egyr.2022.03.009.

[122]	L. Bongini, R. A. Mastromauro, D. Sgrò, and F. Malvaldi, “Electrical Damping Assessment and Stability Considerations for a Highly Electrified Liquefied Natural Gas Plant,” Energies, vol. 13, no. 10, p. 2612, May 2020, doi: 10.3390/en13102612.

[123]	R. D. Zimmerman, C. E. Murillo-Sanchez, and R. J. Thomas, “MATPOWER: Steady-State Operations, Planning, and Analysis Tools for Power Systems Research and Education,” IEEE Trans. Power Syst., vol. 26, no. 1, pp. 12–19, Feb. 2011, doi: 10.1109/TPWRS.2010.2051168.

[124]	A. J. Monticelli, A. Garcia, and O. R. Saavedra, “Fast decoupled load flow: hypothesis, derivations, and testing,” IEEE Trans. Power Syst., vol. 5, no. 4, pp. 1425–1431, Nov. 1990, doi: 10.1109/59.99396.

[125]	M. Huneault and F. D. Galiana, “A survey of the optimal power flow literature,” IEEE Trans. Power Syst., vol. 6, no. 2, pp. 762–770, May 1991, doi: 10.1109/59.76723.

[126]	Xiaokang Xu, M. F. Kandlawala, and Ming Wu, “NERC TPL-001-4 transient voltage performance compliance study - criteria development, study methodology and case studies,” in 2016 IEEE Power and Energy Society General Meeting (PESGM), Boston, MA, USA: IEEE, Jul. 2016, pp. 1–5. doi: 10.1109/PESGM.2016.7741072.

[127]	A. Fernandez-Guillamon, A. Molina-Garcia, K. Das, and M. Altin, “Comparison of different tools for power flow analysis with high wind power integration,” in 2019 International Conference on Clean Electrical Power (ICCEP), Otranto, Italy: IEEE, Jul. 2019, pp. 82–86. doi: 10.1109/ICCEP.2019.8890163.

[128]	V. Geekiyanage and J. Seppänen, “Power System Stability Improvements Through Grid Forming Inverters for Systems with High Penetration of Grid Following Inverters,” in 2024 IEEE PES Innovative Smart Grid Technologies Europe (ISGT EUROPE), Dubrovnik, Croatia: IEEE, Oct. 2024, pp. 1–5. doi: 10.1109/ISGTEUROPE62998.2024.10863434.

[129]	IEEE Standard for the Specification of Microgrid Controllers. doi: 10.1109/IEEESTD.2018.8340204.

[130]	J. S. Ali, Y. Qiblawey, A. Alassi, A. M. Massoud, S. M. Muyeen, and H. Abu-Rub, “Power System Stability With High Penetration of Renewable Energy Sources: Challenges, Assessment, and Mitigation Strategies,” IEEE Access, vol. 13, pp. 39912–39934, 2025, doi: 10.1109/ACCESS.2025.3546491.

[131]	NERC, “Inverter-Based Resource Performance Issues.” [Online]. Available: https://www.nerc.com/globalassets/programs/bpsa/alerts/2023/nerc-alert-r-2023-03-14-01-level-2---inverter-based-resource-performance-issues.pdf

[132]	J. C. Das, Power System Harmonics and Passive Filter Designs, 1st ed. Wiley, 2015. doi: 10.1002/9781118887059.

[133]	M. S. Anindya, F. Zaro, and M. Popescu, “Power Quality Improvement Using Active Power Filters in Industrial Systems,” RESWARA J. Ris. Ilmu Tek., vol. 3, no. 2, pp. 44–50, Apr. 2025, doi: 10.70716/reswara.v3i2.404.

[134]	HOMER, “Microgrid and Hybrid Power Modeling.” [Online]. Available: https://homerenergy.com/

[135]	R. Rogersten, L. Vanfretti, and W. Li, “Towards consistent model exchange and simulation of VSC-HVdc controls for EMT studies,” in 2015 IEEE Power & Energy Society General Meeting, Denver, CO, USA: IEEE, Jul. 2015, pp. 1–5. doi: 10.1109/PESGM.2015.7285986.

[136]	A. N. Rosli, S. H. Yusoff, H. Mansor, S. N. M. Sapihie, and M. A. M. M. Fahmi, “Using Model Predictive Control in Renewable Energy Sources,” in 2023 IEEE 9th International Conference on Smart Instrumentation, Measurement and Applications (ICSIMA), Kuala Lumpur, Malaysia: IEEE, Oct. 2023, pp. 263–268. doi: 10.1109/ICSIMA59853.2023.10373520.

[137]	R. H. Inman, H. T. C. Pedro, and C. F. M. Coimbra, “Solar forecasting methods for renewable energy integration,” Prog. Energy Combust. Sci., vol. 39, no. 6, pp. 535–576, Dec. 2013, doi: 10.1016/j.pecs.2013.06.002.

[138]	U. Cali et al., “Generative AI and LLM applications in renewable energy and smart grids: a systematic review for the sustainable energy transition,” Artif. Intell. Rev., Apr. 2026, doi: 10.1007/s10462-026-11545-2.

[139]	E. Hosseini et al., “Reinforcement learning-based energy management system for lithium-ion battery storage in multilevel microgrid,” J. Energy Storage, vol. 109, p. 115114, Feb. 2025, doi: 10.1016/j.est.2024.115114.

[140]	N. Subramanian and A. A. Stonier, “Digital twin applications and case studies in modern power grid management,” Energy Rep., vol. 15, p. 109218, Jun. 2026, doi: 10.1016/j.egyr.2026.109218.

[141]	H. Chen, X. Feng, Q. Chen, and R. Han, “The Application of Machine Learning in Power Grid,” in 2024 Boao New Power System International Forum - Power System and New Energy Technology Innovation Forum (NPSIF), Qionghai, China: IEEE, Dec. 2024, pp. 568–576. doi: 10.1109/NPSIF64134.2024.10883453.

[142]	R. Schaeffer et al., “Energy sector vulnerability to climate change: A review,” Energy, vol. 38, no. 1, pp. 1–12, Feb. 2012, doi: 10.1016/j.energy.2011.11.056.

[143]	M. A. Bekhti, L. Ghomri, H. L. Beklaouz, and R. Bouddou, “Techno-economic and environmental optimization of standalone hybrid energy systems using advanced energy storage for remote electrification in Southern Algeria,” J. Renew. Sustain. Energy, vol. 17, no. 5, p. 056309, Sep. 2025, doi: 10.1063/5.0297401.

[144]	X. Li, Z. Zhao, X. Jiang, Y. Chen, and R. He, “A Review on AI-Driven Optimization of Data Center Energy Efficiency and Thermal Management,” Int. J. Appl. Sci., vol. 8, no. 3, p. p108, Sep. 2025, doi: 10.30560/ijas.v8n3p108.

[145]	A. Radovanovic et al., “Carbon-Aware Computing for Datacenters,” 2021, arXiv. doi: 10.48550/ARXIV.2106.11750.

[146]	T. Sukprasert, A. Souza, N. Bashir, D. Irwin, and P. Shenoy, “On the Limitations of Carbon-Aware Temporal and Spatial Workload Shifting in the Cloud,” in Proceedings of the Nineteenth European Conference on Computer Systems, Athens Greece: ACM, Apr. 2024, pp. 924–941. doi: 10.1145/3627703.3650079.

[147]	M. D. E. Gouaouri, M. Bagaa, S. Ouahouah, M. A. Ouameur, and A. Ksentini, “Enabling Power-Awareness for Kubernetes Scheduling Through Multi-Criteria Optimization,” in ICC 2025 - IEEE International Conference on Communications, Montreal, QC, Canada: IEEE, Jun. 2025, pp. 1500–1505. doi: 10.1109/ICC52391.2025.11160865.

[148]	S. Sarkar et al., “Carbon Footprint Reduction for Sustainable Data Centers in Real-Time,” 2024, arXiv. doi: 10.48550/ARXIV.2403.14092.

[149]	J. Sefyrin, “Sustainable datacenters and eco-modernist frictions in Sweden,” Inf. Commun. Soc., pp. 1–17, Dec. 2025, doi: 10.1080/1369118X.2025.2596872.

[150]	Lazard, “Levelized Cost of Energy.” [Online]. Available: https://www.lazard.com/media/eijnqja3/lazards-lcoeplus-june-2025.pdf

[151]	EPA, “Summary of Inflation Reduction Act provisions related to renewable energy.” [Online]. Available: https://www.epa.gov/green-power-markets/summary-inflation-reduction-act-provisions-related-renewable-energy

[152]	M. S. Hoosain, B. S. Paul, S. Kass, and S. Ramakrishna, “Tools Towards the Sustainability and Circularity of Data Centers,” Circ. Econ. Sustain., vol. 3, no. 1, pp. 173–197, Mar. 2023, doi: 10.1007/s43615-022-00191-9.

[153]	NFPA, “NFPA 110 Type 10 Requirements for Emergency Power Systems.” [Online]. Available: https://www.cummins.com/sites/default/files/2019-03/PowerHour_NFPA110.pdf

[154]	R. Kasperzak, M. Kureljusic, L. Reisch, and S. Thies, “Accounting for Carbon Emissions—Current State of Sustainability Reporting Practice under the GHG Protocol,” Sustainability, vol. 15, no. 2, p. 994, Jan. 2023, doi: 10.3390/su15020994.

[155]	G. Soyturk and O. Kizilkan, “Modeling and analysis of solid oxide fuel cell-based multigeneration system with supercritical and transcritical carbon dioxide power cycles, humidification-dehumidification system and hydrogen generation,” Energy Convers. Manag., vol. 332, p. 119762, May 2025, doi: 10.1016/j.enconman.2025.119762.

[156]	Arthur D. Little, “U N L O C K I N G FUSION ENERGY.” [Online]. Available: https://www.adlittle.com/sites/default/files/reports/ADL_Unlocking_fusion_energy_2025%20%281%29.pdf

[157]	F. M. A. Hadi, H. H. Aly, and T. Little, “Harmonics Forecasting of Wind and Solar Hybrid Model Based on Deep Machine Learning,” IEEE Access, vol. 11, pp. 100438–100457, 2023, doi: 10.1109/ACCESS.2023.3314742.

[158]	M. I. Saleem, S. Saha, U. Izhar, and L. Ang, “Stability assessment of inverter‐based renewable energy sources integrated to weak grids,” IET Energy Syst. Integr., vol. 6, no. 4, pp. 525–544, Dec. 2024, doi: 10.1049/esi2.12151.

[159]	N. Institute, “Beyond FERC Order 2023: Considerations on Deep Interconnection Reform”, [Online]. Available: https://www.researchgate.net/publication/382074664_Beyond_FERC_Order_2023_Considerations_on_Deep_Interconnection_Reform

[160]	S. Talebi and H. H. Aly, “Optimized Renewable Energy Integration: Advanced Modeling, Control, and Design of a Standalone Microgrid Using Hybrid FA-PSO,” IEEE Access, vol. 13, pp. 63486–63503, 2025, doi: 10.1109/ACCESS.2025.3559725.

[161]	H. Chen, Z. Zhang, C. Guan, and H. Gao, “Optimization of sizing and frequency control in battery/supercapacitor hybrid energy storage system for fuel cell ship,” Energy, vol. 197, p. 117285, Apr. 2020, doi: 10.1016/j.energy.2020.117285.

[162]	J. Lu, R. Xiong, J. Tian, C. Wang, and F. Sun, “Deep learning to estimate lithium-ion battery state of health without additional degradation experiments,” Nat. Commun., vol. 14, no. 1, p. 2760, May 2023, doi: 10.1038/s41467-023-38458-w.

[163]	S. Chatterjee, “Mitigating Supply Chain Malware Risks in Operational Technology: ChallengesModellingutions for the Oil and Gas Industry”.

[164]	M. G. Todeschini, G. Dondossola, and R. Terruggia, “IMPACT EVALUATION OF IEC 62351 CYBER SECURITY ON IEC 61850 COMMUNICATIONS PERFORMANCE,” 2019.

[165]	A. Dimakopoulou and K. Rantos, “Comprehensive Analysis of Maritime Cybersecurity Landscape Based on the NIST CSF v2.0,” J. Mar. Sci. Eng., vol. 12, no. 6, p. 919, May 2024, doi: 10.3390/jmse12060919.

[166]	M. Dukan and B. Steffen, “Cost of capital for renewables and enabling technologies: Measuring the multidimensional heterogeneity in Switzerland,” 2024, SSRN. doi: 10.2139/ssrn.4926798.

[167]	O. Kay, R. Reaser, and R. Taylor, “Processing Power: The Effect of Data Centers on Wholesale Electricity Markets,” Fed. Reserve Bank Dallas Work. Pap., vol. 2026, no. 2606, Mar. 2026, doi: 10.24149/wp2606.

[168]	G. Duppati, “Carbon pricing and revenue growth valuation risk exposure,” Int. Rev. Econ. Finance, vol. 103, p. 104442, Oct. 2025, doi: 10.1016/j.iref.2025.104442.

[169]	Daniel Yang, “Risk Structure and Financial Hedging in Nodal Electricity Markets.” [Online]. Available: https://www.oxfordenergy.org/wpcms/wp-content/uploads/2026/01/EL-61-Risk-Structure-and-Financial-Hedging.pdf

[170]	J. Commins and K. Irion, “Towards Planet-Proof Computing:Ten Key Elements EU Data Center Sustainability Policy Should Take Onboard,” Eur. Law Blog, Mar. 2025, doi: 10.21428/9885764c.f93298cf.

[171]	Alistair Baker-Brian, “Data Centers in 2026: 5 Trends Reshaping Power, Cost, and Resilience.” [Online]. Available: https://www.enersys.com/en/blog-articles/data-centers-five-trends-reshaping-power-cost-and-resilience/

[172]	F. Kahrl, J. H. Kim, A. Mills, R. Wiser, C. Montañés, and W. Gorman, “Variable Renewable Energy Participation in U.S. Ancillary Services Markets”.

[173]	R. Abritta et al., “Power Flow-Based Estimation of Short-Circuit Currents From Inverter-Based Resources,” IEEE Open Access J. Power Energy, vol. 13, pp. 229–239, 2026, doi: 10.1109/OAJPE.2026.3673646.

[174]	i2X, “Transmission Interconnection Roadmap.” [Online]. Available: https://www.energy.gov/sites/default/files/2024-04/i2X%20Transmission%20Interconnection%20Roadmap.pdf

[175]	J. Rand et al., “Up: 2025 Edition, Characteristics of Power Plants Seeking Transmission Interconnection As of the End of 2024,” 2025, doi: 10.13140/RG.2.2.12274.67520.

[176]	UN, “ENVIRONMENTAL COST OF AI’S ENERGY USE.”

[177]	Alexander Heiss, Zacharias Sautner, and Zacharias Sautner, “Powering AI: How Do Data Centers Affect Renewable Energy Investment?” [Online]. Available: https://papers.ssrn.com/sol3/papers.cfm?abstract_id=6426079

[178]	IESO, “2026 Annual Planning Outlook.” [Online]. Available: https://www.ieso.ca/-/media/Files/IESO/Document-Library/planning-forecasts/apo/2026/2026-APO-Demand-Forecast-Module.pdf

[179]	P. A. Vilchez Olivares and B. J. Astorga De La Cruz, “AI and Data Analytics in Sustainable Financial Reporting and ESG Disclosure: A Systematic Literature Review,” Sustainability, vol. 18, no. 11, p. 5393, May 2026, doi: 10.3390/su18115393.

[180]	C. D. Schuman, S. R. Kulkarni, M. Parsa, J. P. Mitchell, P. Date, and B. Kay, “Opportunities for neuromorphic computing algorithms and applications,” Nat. Comput. Sci., vol. 2, no. 1, pp. 10–19, Jan. 2022, doi: 10.1038/s43588-021-00184-y.

[181]	T.-C. Hsueh, “Panel-Scale Reconfigurable Photonic Interconnects for Scalable AI Computation”.

[182]	Y. Ding, Z. P. Cano, A. Yu, J. Lu, and Z. Chen, “Automotive Li-Ion Batteries: Current Status and Future Perspectives,” Electrochem. Energy Rev., vol. 2, no. 1, pp. 1–28, Mar. 2019, doi: 10.1007/s41918-018-0022-z.

[183]	A. Kushwaha, K. Ravish, P. Lamba, and P. Kumar, “A Survey of Safe Reinforcement Learning and Constrained MDPs: A Technical Survey on Single-Agent and Multi-Agent Safety,” Apr. 29, 2026, arXiv: arXiv:2505.17342. doi: 10.48550/arXiv.2505.17342.

[184]	R. Eriksson, N. Modig, and K. Elkington, “Synthetic inertia versus fast frequency response: a definition,” IET Renew. Power Gener., vol. 12, no. 5, pp. 507–514, Apr. 2018, doi: 10.1049/iet-rpg.2017.0370.

[185]	H. Nikafshan Rad, A. Ghasemi, and M. Marefati, “Cost and environmental analysis and optimization of a new and green three-level waste heat recovery-based cogeneration cycle: A comparative study,” Heliyon, vol. 10, no. 7, p. e29087, Apr. 2024, doi: 10.1016/j.heliyon.2024.e29087.