Type of the Paper (Article, Review, Communication, Perspective, Editorial, etc.)

Optimizing Energy Infrastructure for AI Data Centers

A Framework for Integrating Renewable Energy Sources

Firstname Lastname 1, Firstname Lastname 2 and Firstname Lastname 2,*

1 Affiliation 1

2 Affiliation 2

* Correspondence: e-mail@e-mail.com

Abstract: Intense growth of Artificial Intelligence (AI) workloads has driven the global data center electricity market to hit new highs with demand expected to rise to around 945 TWH in 2030 from a level of about 415 TWH currently. The challenge of the exponential growth path is to satisfy energy needs of AI infrastructure while also delivering climate goals and economic sustainability. The seven-component design framework introduced in this paper covers the technical, economic and regulatory dimensions of sustainable computing infrastructure. This framework combines site assessment, technology selection, electrical architecture design, hierarchical control strategies, flexibility of the workload on the demand side, economic viability analysis, and sustainability compliance. After conducting a comprehensive literature review which included more than 260 peer-reviewed articles, industry reports and policy documents, this study was synthesized combining current knowledge pertaining to renewables technologies, energy storage, power system modeling and operational strategies. It is supported in detail with case studies from a group of global technology companies that provide cost competitive electricity delivery at $35 – $100/MWh that align with reliability targets to > 99.9%. One conclusion from the key findings is that lithium-ion battery prices are projected to fall to less than $108/ kWh in 2026, with the costs of solar PV installed showing a reduction of more than 90% since 2010, and wind-solar complementarity is expected to slash the need for storage capacity by 40 to 60% using geographic diversification. The paper shows detailed economic modelling including levelized cost of energy (LCOE) calculations, net present value (NPV) analysis and sensitivity assessments, proving pay back periods of 5-12 years with current tax incentives. A multi-year implementation plan has been outlined from 2024 to 2045, alongside the transition of 100% renewable-powered AI data centers into mainstream infrastructure. A multi-year implementation plan has been proposed, starting with demonstration projects, and a journey towards mainstream adoption of 100% renewable-powered AI data centers.

Keywords: AI data centers, renewable energy integration, energy storage, microgrid optimization, power system modeling, demand-side management, carbon-free energy, levelized cost of energy

1. Introduction

## 1.1. Global Data Center Energy Consumption and AI workload Growth

In the last ten years, the whole digital infrastructure has been revolutionized, and the main driver behind this is the explosion of applications based on Artificial Intelligence. The data centers alone were a huge component of this infrastructure and used about 415 TWh of electricity in 2024, which is about 1.5% of world[1], [2]. According to the International Energy Agency (IEA) this consumption may grow to 945 TWh by 2030 based on current growth rates, mainly due to training and inferring workloads of AI models[3]. This is a staggering leap, feeding the electricity use of a power-hungry country the size of Japan into the global grid in just six years, and shows just how critical it is to move towards sustainable energy solutions in data center operations.

This challenge is starkly evident in the energy consumption of specific AI models. To train GPT-3, a 175-billion-parameter language model developed by OpenAI, it required the use of around 1,287 MWh of electricity, which corresponds to an estimated CO2 equivalent emission of 552 tonnes[4], [5]. The next GPT, with significantly more parameters, would have had an even greater cost to energy. Exact numbers are still proprietary, but such a model would likely have been even more costly on a per-use basis. The model called BLOOM [6] is an open-source model consisting of 176 billion parameters that took around 433MWh in training. These are numbers of single training events; the total amount of energy used by constant inferences per year to serve billions of user queries is much higher than training energy. According to research by Li, every inference query of GPT-3 consumes around 2.9 Wh of electricity and adds up to a massive amount with the millions of queries that take place every[7].

One of the biggest tipping points in electricity demand growth since the electrification of industry will come with AI, when This Research [8] division estimated power demand in data centers would grow at a 165% rate by 2030. However, the Power Usage Effectiveness (PUE) of the surveyed locations did not see any significant gains in efficiency as measured by PUE, according to the Uptime Institute 2024 Global Data Center Survey[9]. Meanwhile, AI-specific accelerators such as the NVIDIA H100 GPU, with a thermal design power (TDP) of up to 700 watts per unit, are pushing compute density to levels that challenge conventional cooling and power delivery architectures[10].

Figure 1 Global data center electricity consumption and projections (2015-2030). Source: IEA, 2025

## 1.2. The Renewable Energy Imperative

Three simultaneous drivers, climate goals, cost trends and growing technical viability, are coming together in data center power systems for the integration of renewable energy sources. With over 130 countries aligning themselves to reach carbon zero emissions by 2050 under the Paris Agreement, and the information technology sector has emerged as a critical focus area for decarbonization efforts[11]. Major technology firms such as Google, Microsoft and Meta have all committed to running 24/7 carbon-free energy (CFE) operations by 2030 — a criterion that includes matching all hours of electricity use with clean generation, not accounting for it on an annual basis using renewable electricity certificates (RECs)[12].

The price curve of renewable energy technologies has reshaped how data centers buy power. PV module prices dropped by more than 90% since 2010, to about $0.15 to $0.25 per watt for commercial-grade modules in 2024, and PV system costs for ground mounted utility-scale systems are approximately $0.75 to $1.40 per watt[13], [14]. Onshore wind has also performed well, giving capacity factors in the range of 25 to 40% and Levelized Cost of Energy (LCOE) in the range of $25 to $45 per MWh, placing onshore wind among the most cost-competitive electricity generation technologies for the world[15], [16]. Bloomberg New Energy Finance (BNEF) estimates that battery energy storage system (BESS) prices dropped significantly from $300/kWh in 2020 to $108/kWh in 2025, according to its annual survey[17].

Advances in inverter technology, grid-forming control algorithms and advanced energy management systems have made technical feasibility a lot stronger. Nonetheless, non-synchronous generator grid forming inverters can now offer synthetic inertia, voltage and frequency regulation functions previously available only from synchronous generators, allowing for an increased penetration level of Variable Renewable Energy (VRE) to ensure grid stability without compromising the inherent benefits of VRE[18]. At the same time, the rise and development of advanced load management strategies, such as AI workload scheduling and demand response participation, offer new tools for managing load and demand in real-time[19].

## 1.3. Core Challenges in Renewable Integration

Despite favorable economic and technological trends, significant challenges remain in achieving reliable, renewable-powered data center operations. Solar and wind generation has inherent intermittency that makes it difficult to match up the supply and demand at the transmission level; managing this mismatch combines energy storage, demand flexibility, and expansion of the grid[20]. Rapid variations in solar power due to cloud cover can mean that it drops by 60-90% in just a few minutes; similarly hourly changes in wind generation could be 30-50% without wind interruptions[21]. These variability patterns need storage systems to span gaps of hours depending on resource profile and load requirements.

Another key issue is power quality. A high amount of harmonic distortion is produced by data centre loads, especially for computing loads employing switched-mode power supplies (SMPS). The number of modern nonlinear loads, such as the variable frequency drive (VFD) for cooling system, and LED lights, adds to the total harmonic distortion (THD) which should not exceed 5% based on IEEE 519 standards[22]. The addition of inverter-based renewable energy sources introduces additional harmonic sources, requiring careful design of filtering and power conditioning systems to maintain compliance with power quality standards.

More complex grid interconnection is an enormous hindrance to deployment. However, for congested grid areas like those currently experiencing queues of 3-5 years for studies with $50,000 to $500,000 and grid upgrades potentially running into the $10 million range, as is currently the case with (California ISO) CAISO and Pennsylvania-New Jersey-Maryland Interconnection (PJM) in the United States[23]. In July 2023, Federal Energy Regulatory Commission (FERC) issued Order 2023 to streamline the interconnection process for inverter-based resources by establishing standardized procedures and timelines for interconnection applications [24] where its implementation of the Order will take several years.

## 1.5. Research Gap and Paper Statement

Although there are numerous works on individual aspects of renewable electricity integration, in practical terms, a considerable lack of comprehensive studies exists that account for all aspects of the process of designing and operating a data center with renewable power. Most of the published literature has concentrated in one of two ways: either on the technical side of power systems or the economic side of energy procurement with no attempt to integrate both which is often absenting any single framework[25]. Further, the dynamic nature of AI workloads, with small shifts to ever more power dense accelerators, necessitates analysis that is in line with the latest hardware capabilities and their impact on creating effective infrastructure implementations[26].

The gap mentioned above is addressed in this paper by proposing and testing a seven-components framework for designing, deploying, and deploying renewable powered AI data centers. The framework covers the following:

(1) Site assessment and resource evaluation,

(2) Technology mix optimization,

(3) Electrical architecture and integration design,

(4) Hierarchical control and dispatch strategies,

(5) Demand-side workload flexibility,

(6) Economic viability modelling, and

(7) Resilience and sustainability compliance.

The main argument is that hybrid systems integrating renewable energy generation, energy storage, power grid interconnection, and demand-side flexibility can enable economically sustainable, environmentally friendly, and highly reliable operation of AI data centres in various geographical and climatic settings.

Chapter 2 includes a detailed review of the state of the art, Chapter 3 covers the fundamentals of electricity, Chapter 4 covers the characterisation of renewable energy resources, Chapter 5 deals with energy storage technologies, Chapter 6 with power system modeling and simulation, Chapter 8 with case studies, Chapter 9 with technical challenges and Chapter 10 with economics analysis, Chapter 11 with operational strategies and Chapter 12 with regulatory considerations, Chapter 13 with future research directions and Chapter 14 summarises the conclusions and recommendations.

2. Literature Review and State-of-the-Art

This chapter synthesizes the existing body of knowledge across five domains critical to renewable-powered AI data centers: data center power consumption, renewable energy technologies, energy storage systems, microgrid and grid integration, and industry case studies. The review draws upon over 160 sources published between 2015 and 2025, with emphasis on the most recent and impactful contributions.

## 2.1. AI Data Center Power Consumption

Unlike traditional enterprise data centers, AI data centers have different power consumption characteristics because the workloads on GPUs and TPUs are of a high intensity and concentrated nature. Unlike older AI accelerators, such as the NVIDIA H100 Tensor Core GPU, which come in a variety of thermal envelope sizes, ranging from 350W to 700W per unit, the SXM is significantly more power-hungry than the PCIe version [10], [27]. Power densities can reach 30 kW on the rack with eight GPUs per server and multiple servers per rack, whereas typical enterprise computing rack power densities are 5 to 10 kW[28]. This significant increase in compute density has far-reaching impacts on power delivery infrastructure, cooling system design and facility power usage.

The intensity and timing of training varies from inference. Training is designed to use high and near maximum power for hours to weeks and has little or no "idle" time between computation cycles[4], [29]. Inference workloads are more variable in that power consumption can vary depending on the number of requests, model complexity, and the batch size. Research shows that training loads generally use 80-95% of the peak GPU power, and inferences use 40-70% of the peak GPU power, depending on the application and traffic [30]. The temporal pattern of load has important implications for integration planning for renewable energy, as the length of time they are stored and dispatched will depend on this.

The most widely used measure for the energy efficiency of a data center is called Power Usage Effectiveness (PUE), which is calculated as the ratio of total facility power to IT equipment power. The Uptime Institute 2024 Global Data Center Survey, which drew results from almost 900 operators around the world, found an industry average PUE of 1.56, and facilities with the lowest scores had a PUE of 1.06 [9]. The survey, however, found that there has been little improvement in PUE in the last five years, as the overall average value has not significantly changed since 2019. The plateau is blamed on rising power needs of these accelerators, as efficiency advances in power distribution and cooling have failed to keep up. Generally, Google's plants have been at the forefront of the PUE front, with a trailing 12-month average of 1.10 across the worldwide fleet of the company, thanks to the use of advanced cooling systems, custom server design and AI-based temperature management[31].

The second most energy intensive energy consumer in data centres is the cooling system consuming between 30-50% of the total energy used by the data centre facility[32], [33]. The classic way of cooling has its limitations in high density AI deployments where the heat generation per square meter can surpass what can be achieved by using a conventional computer room air conditioning (CRAC) system. Liquid cooling is a technology that can provide significant efficiency gains, down to 40% of cooling energy compared to air-based cooling [34]. The next-generation data center designs by Microsoft use no water to cool the data center, and are at the forefront of cooling technology for AI workloads[35].

## 2.2. Renewable Energy Technologies

In the last 10 years, solar PV technology has experienced an incredible cost and performance shift. The efficiencies of mainstream commercial modules have increased from 15-17% in 2016 to 21-23% in 2026, with efficiencies of 24- 25% for premium modules achieved by advanced TOPCon, Heterojunction (HJT), and Back Contact (BC) cell architectures[36]. The efficiency of the inverter has also improved, and modern string and central inverters can achieve 95-98.5% weighted efficiency under different load conditions[37]. The levelized cost of electricity for utility scale solar PV has dropped to $30 to $50/MWh in high resource areas and is the lowest cost source of new electricity generation in most markets globally[38], [39].

The technology of wind power has progressed greatly and onshore wind turbines can reach capacity factors of 25-40%, with optimal offshore wind installations reaching 40-50%[40]. Onshore wind had a global weighted average LCOE of $0.034 per kWh, making it the most cost-competitive new power generation technology in the world, according to the IRENA Renewable Power Generation Costs report[16]. The use of LiDAR technology and numerical weather prediction has improved wind resource assessment, which allows for better siting decisions and energy yield estimates[41]. Wind and solar generation are naturally complementary because wind tends to generate more energy during the night and winter months, when solar generation is minimal, and solar generation is more dominant during the day and summer months when wind generation is low, resulting in a natural way to reduce the aggregate variability in hybrid systems[42].

Hydroelectric power, specifically pumped-storage hydropower (PSH), is a vital component in the energy balancing equation at the grid level. PSH makes up about 95% of the world's electricity storage capacity and offers gigawatt hours of storage at much lower costs than battery systems[43]. Run-of-river hydroelectric schemes are well suited to baseload generation, with relatively low environmental impacts, whereas reservoir systems enable storage for periods of a few weeks, which is necessary to account for the variability of renewable energy over the course of a year[44]. New hydroelectric development is however constrained by geography and environmental permitting in many regions, limiting scalability.

## 2.3. Energy Storage Technologies

The stationary storage market is dominated by lithium-ion battery technology, which is expected to drop from about $300/kWh in 2020 to $108/kWh in 2025 as reported by BloombergNEF's annual survey[17]. The low cost, higher cycle life (more than 4,000 cycles at 80% depth of discharge) and the safer safety profile of LFP chemistry (lithium iron phosphate) make it the most preferred chemistry for stationary applications, as compared to NMC (nickel manganese cobalt) chemistry and NCA (nickel cobalt aluminum) chemistry[45], [46]. The round-trip efficiency of lithium-ion systems is 85-95%, and thermal management systems are needed to ensure optimal operating temperatures and to maximize calendar life.

With greater storage times than 8 hours, long-duration energy storage (LDES) technologies are gaining traction. Vanadium Redox Flow Batteries (VRFBs) have high cycle life (20,000+ cycles) and can be highly scalable in terms of duration with independent power and energy sizing, but with higher initial costs[47]. The iron-air battery technology developed by Form Energy is being deployed in multi-GWh projects, aiming for storage costs of $20/kWh and durations longer than 100 hours, which could mark a paradigm shift for seasonal energy storage[48]. The storage period of green hydrogen is weeks to months, but with a round trip efficiency of 50-60% and current costs ranging from $150 to $250/MWh[49].

Energy storage sizing methodologies have evolved from simple deterministic approaches based on worst-case scenarios to sophisticated probabilistic and optimization-based frameworks. The probabilistic approach uses metrics such as Loss of Load Expectation (LOLE) to quantify reliability, where LOLE represents the expected number of hours per year that available generation is insufficient to meet demand [50]. Optimization-based approaches solve the sizing problem as a mixed-integer linear program (MILP) to minimize the total system cost while satisfying reliability constraints, carbon emission limits and capacity constraints for interconnection[51].

## 2.4. Microgrids and Grid Integration

With the growing inverter-based resource (IBRs) penetration, microgrid control strategies have progressed considerably. The concept of grid-forming inverters is a paradigm shift from grid-following designs that use phase-locked loops (PLLs) to synchronize with the grid frequency[52]. The IEEE 2800-2022 standard was developed specifically for inverter-based resources and defines performance criteria for frequency response, voltage support and ride-through that allow for reliable operation at high levels of renewable penetration[53]. FERC Order 2023 also clarifies the interconnection process, providing streamlined timelines and pre-certification routes to mitigate delays in the queue[24].

In data center microgrids, harmonic distortion, power factor correction, and voltage regulation are important considerations for power quality management. The IEEE 519 specifies a THD limit of less than 5% at the point of common coupling (PCC), and individual harmonic limits of 3% for characteristic harmonics[22]. SMPSs, VFDs, and LED drivers are examples of nonlinear loads in today's data centers that can produce substantial harmonic currents resulting in transformer overheating, capacitor bank damage, and overload of the neutral conductor if left unchecked[54]. In high-density computing, active power filter and multi-pulse rectifier topologies are effective solutions for harmonic compliance.

## 2.5. Industry Case Studies

Google has become an industry leader in buying renewable energy. The company has recently increased its contracting activities, resulting in a portfolio of more than 30 GW of total clean energy capacity worldwide from over 170 power purchase agreements (PPAs)[55]. Google met its hourly carbon-free energy (CFE) matching metric at 64% on a worldwide basis, and continues on its path toward achieving its structural target of 100% CFE operation on all regional grids by 2030[55], [56]. This approach involves the deployment of a 50 MW on-site wind generation framework at its data center cluster in Iowa, along with more than 200 MW of wind and solar PPAs in Chile. The strategy of Google's architecture is to spread out their architecture geographically, taking advantage of the anti-correlated, complementary nature of wind assets in the U.S. Midwest and solar assets in the Southwest to significantly reduce the overall variability of the grid they are tied to[56].

Meta has taken a differentiated approach, focusing on localized fuel cell deployment and extensive grid additionality. Meta has installed 5 MW of SOFCs at its Prineville, OR data center campus to supply stable primary baseload power[56]. Since 2020, Meta has been structurally matching its operational electricity consumption with clean energy additions annually, with contracted wind and solar capacity now representing nearly 29 GW of clean energy capacity on a global basis [57], [58].

At the same time, Microsoft has been leading the way with very decentralized baseload ideas. This includes Project Natick, an underwater data centre deployment that achieved a 99.9% uptime reliability factor and an eight-fold reduction in hardware failure rates compared with traditional land-based data centers[59], [60]. In order to support the very large workloads of AI, Microsoft has transitioned to the nuclear energy frameworks, with direct, long-term power supply relationships that provide stable, non-intermittent baseload power that is carbon-free[61].

Equinix is the world's largest colocation data center provider with a presence in more than 260 facilities, which manages a very decentralized clean energy procurement architecture[62]. Equinix has established a 96% global renewable energy coverage metric for its retail data center portfolio, with multiple hundreds of megawatts of solar and wind capacity across California, Arizona, Texas, and Europe[63].

Likewise, Apple has removed its operating footprint and matched 100% renewable energy at its corporate operations and upstream manufacturing supply chain. This setup includes a specialized 10 MW solid oxide fuel cell array at its Maiden, North Carolina data center, running in parallel with significant onsite solar power generation. These are clearly public-facing corporate efforts to prove that although perfect, real-time 24/7 CFE matching is a continuing challenge on the grid, utility-scale renewable-powered data center configurations are technically stable and economically better options for hyperscale infrastructure[64].

3. Electrical Fundamentals of Data Center Systems

## 3.1. Electrical Distribution Architecture

The electrical distribution system in a data center is hierarchical, stepping down the voltage from the utility interconnection levels to the low voltage levels needed by the computing systems. Primary interconnection usually takes place at medium-voltage (MV) levels of 13.8 kV or 25 kV, and step-down transformers step down the voltage to levels required for facility distribution at 4.16 to 6.9 kV[65]. Power distribution units (PDUs) deliver 480 V three-phase power to the last-mile for individual equipment racks.

It is one of the most important design parameters and is classified by the Uptime Institute Tier Standard as N (no redundancy), N+1 (one spare component), N+2 (two spare components), 2N (fully redundant, dual path), or 2(N+1)[66]. The typical configuration for most AI data centers is 2N, which means that each critical load is connected to two separate power paths, and the power paths are configured to switch automatically when one fails. The redundancy model also affects capital costs: For 2N designs, electrical infrastructure costs are generally 80 to 100% higher than those for N+1 designs; and, in the case of single-component failures, 2N designs offer essentially zero downtime[67].

Power is distributed from the utility interconnection point through main switchgear that provides protection coordination and metering, to automatic transfer switches (ATS) that control the transfer of power from the utility to the backup power source during a power outage. In high-reliability applications, the transfer time is less than 1 cycle (16.7ms) for static transfer switches (STS) and 10-30s for electromechanical switches (EMS) in the ATS[68]. AI training workloads are typically specified with STS or flywheel-based uninterrupted power supply (UPS) systems, as a brief power interruption can disrupt the workloads.

## 3.2. AI Workload Electrical Charactersitics

Modern AI accelerators exhibit distinctive electrical characteristics that differentiate them from conventional server loads. The NVIDIA H100 SXM GPU is rated up to 700 W, while the previous generation A100 has a maximum TDP of 250 to 400 W. Each HGX H100 server is equipped with eight GPUs, yielding a peak server power consumption of more than 10 kW when all eight GPUs are in operation, which includes memory, networking, and cooling system components. These systems generate localized load pockets that consume 30 to 50 kW per rack as compared to enterprise computing, which consumes 5 to 10 kW per rack[10].

GPU power states are heavily dependent on the workload. During the model training phase, GPUs can draw power close to their TDP under full computational load, depending on the computational operations (e.g., matrix multiplication, memory access, communication)[69]. Idle power consumption is usually in the range of 50-150 W per GPU, or about 15-20% of peak power, because memory contents must be kept alive and providing low-latency response for inference operations[70]. Power capping (e.g. using NVML power limit API) allows operators to cap the max power draw for lower computational throughput, offering a power management solution for the demand side.

Thermal design point considerations shall include steady state and transient thermal loads. GPU temperatures during training can reach 80-85 degrees Celsius when the GPUs are sustained under load, and cooling systems must be able to dissipate 3.5-5 kW of cooling power per GPU[71]. The electrical energy that is input to computing equipment is almost entirely converted to heat, which is why there is a very close relationship between electrical energy consumption and heat generation. This integration of electrical and thermal systems opens the opportunity to integrated energy management, optimizing the operation of the cooling system with the availability of renewable energy and the optimization of the workload.

## 3.3. Backup Power and UPS Systems

UPS system is the first line of defense against power quality disturbances and short outages. There are three major UPS technologies used in data centers: flywheel systems, which can deliver 10-30 seconds of ride-through time with kinetic energy storage; battery-based UPS, which can supply minutes to hours of backup time depending on the battery capacity; and hybrid UPS, which includes flywheels to provide immediate response and batteries to provide extended backup time[72]. AI data centers, where training state can be lost during even brief interruptions, require UPS systems to have enough runtime to start-up and synchronize the backup generator, usually 30 to 60 seconds[73].

The UPS capacity needed for a 100 MW data center with N+1 redundancy and 20% safety margin would be about 144 MVA with a power factor of 0.9[74]. The choice of the double-conversion (online), line-interactive, and standby (offline) UPS topologies depends on the criticality of the load. Data center AI training and inference workloads are typically designed with double-conversion topology, ensuring full protection from input power disturbances[75].

The most widely used backup power system for data centers is a diesel generator, which is sized based on the peak facility load with an updated safety capacity utilization buffer of 15-25% to effectively suppress severe localized voltage fluctuation caused by sudden load increases from AI inference workloads and power-electronic harmonic distortion. For a 100 MW hyperscale generator size configuration, the size of each generator is typically between 20 and 30 MW, and they are arranged in parallel across multiple isolated dual-bus distribution paths to ensure redundant N+1 or 2N topology benchmarks[76]. Despite the proven efficiency of diesel generators, they generate very high levels of nitrogen oxides (NOx) during routine testing, up to 12 metric tons per year per hyperscale facility, having a direct impact on urban air quality margins and increasing the pace of reaching localized greenhouse gas thresholds[77]. As a result, the industry is moving into new directions of cleaner fuels, growing interest in natural gas generators at utility scale, and grid integration of hydrogen fuel cell systems that not only provide onsite mission-critical backup power but now deliver fast-frequency ancillary services back to the main grid as well.

## 3.4. Colling System Integration

Cooling systems are a crucial connection point between electrical and thermal management in AI data centers. Cooling load and electrical energy consumption are roughly proportional, with the coefficient of performance (COP) of the cooling system dictating the number of watts of cooling for every watt of electricity consumed (typically around 2.5 to 4)[78]. Cooling consumption can be as high as 30-40% of the total facility energy cost for traditional air-cooled data centers, which can have PUE values of greater than 1.3[32]. Immersion cooling provides 30-50% reduction in cooling energy by taking advantage of the superior heat transfer properties of liquids over air, and can be implemented in a variety of ways such as direct-to-chip cold plates, rack-level cooling loops, and full immersion cooling[34].

In suitable climates, significant energy savings can be realized by using a free cooling system, which utilizes the ambient atmospheric temperature to supply cooling without mechanical refrigeration. In temperate climates, economizer systems can deliver free cooling for 3000 to 6000 hours per year, cutting energy consumption for chillers by 40-70% during those hours[79]. Thermal energy storage (TES) systems, particularly ice storage, allow the shifting of cooling loads when electricity demand is high and/or renewables are plentiful by freezing water when electricity prices are low, and release it during periods of high cooling demand and electricity prices.Thermal energy storage (TES) systems, specifically ice storage, can be used to shift cooling loads when electricity demand is high, and/or when renewables are abundant, by freezing water when electricity prices are low, and melting when electricity prices are high, and cooling loads are high[80].

## 3.5. Power Quality and Harmonic Analysis

Harmonic currents create voltage waveshapes which are distorted from their ideal sinusoidal nature in non-linear loads within a data center, resulting in equipment malfunction, loss of efficiency, and early failure. The main sources of harmonics are switched-mode power supplies (SMPS) in servers and networking devices, variable frequency drives (VFDs) in cooling systems, and LED lighting drivers[81]. According to IEEE 519-2022, the maximum allowed total harmonic distortion (THD) at the point of common coupling (PCC) is 5%, while the limits for the individual harmonics range from 3% for lower-order harmonics to lower limits for higher-order harmonics[22]. Passive filters (tuned LC circuits targeting specific harmonic orders), active power filters (APFs) that inject compensating currents to cancel harmonic distortion, and system level solutions, such as 12-pulse or 18-pulse rectifier configurations that naturally cancel lower order harmonics[82] are all available as options for mitigation. The use of power factor correction (PFC) circuits in the modern server power supply has minimized the harmonic contribution from IT equipment, and most modern servers have a power factor > 0.95 and THD < 10% at the input terminals[83]. The overall impact of thousands of nonlinear loads, however, is best addressed through facility-level harmonic analysis and mitigation.

## 3.6. Metering and Monitoring Systems

Energy management and optimization are built on comprehensive metering and monitoring infrastructure, which ensures real-time data foundation. Revenue-grade power meters are usually ANSI C12.20 Class 0.2 accuracy and are used at key distribution points such as utility interconnections, generator outputs, UPS inputs and outputs, and PDU feed circuits[84]. Today's energy management systems (EMS) are designed to collect data from hundreds or thousands of metering points, give a dashboard, trending, alarm management and automate reporting. The system can be integrated with building management systems (BMS), which allows for the correlation of electrical consumption with environmental conditions and cooling system performance. Modern EMS platforms provide data logging and analytics features that allow for more advanced efficiency optimization, such as identifying lost energy in equipment not being used, tracking unusual energy use patterns which can signify equipment deterioration, and comparing actual energy use to predicted energy use based on weather, occupancy, and workload parameters[85]. Machine learning algorithms have been shown to lower cooling energy use by 15-30% by optimizing setpoints and scheduling equipment in EMS[86].

4. Renewable Energy Resources and Assessment

This chapter characterizes the solar, wind, and hydroelectric resources available for data center integration, along with the methodologies used to assess these resources and quantify their variability. Understanding resource characteristics is fundamental to optimal technology selection, system sizing, and operational strategy development for renewable-powered data centers.

## 4.1. Solar Photovoltaic Systems

PV is now the least expensive renewable energy option in most geographies for data centers where the sun shines. Currently available monocrystalline modules in the commercial market have efficiencies of 20–23%, while high-efficiency modules with heterojunction (HJT) or tunnel oxide passivated contact (TOPCon) cell architectures have achieved efficiencies of 23–25% under standard test conditions [13]. According to the latest global market indicators, the weighted average cost of utility-scale ground-mounted solar PV systems has continued its historic decline, sitting between $0.70 and $1.30/W ($700 to $1,300/kW) in the current market, marking an approximate 87% to 90% drop from 2010 benchmarks [14]. This downward cost trajectory is sustained by industry capacity, with IRENA’s latest 24/7 power analytics projecting an additional 30% reduction in firm solar-plus-storage configuration costs by 2030, eventually dipping beyond 40% by 2035[36].

The geographic variability of solar capacity factors is high, with values ranging from 13-17% in the northern part of Europe and the Pacific Northwest, to 25-30% in the desert Southwest of the U.S. and arid areas of the Middle East and North Africa[87]. NREL's Annual Technology Baseline reports net capacity factors spanning 21-34% for utility-scale PV across solar resource classes[88]. The performance of the inverter is a key factor; modern string and central inverters provide weighted average efficiencies of 95-98.5% under varying irradiance and temperature conditions. Going beyond basic energy conversion, advanced inverter functions such as reactive power control, voltage ride-through, and dynamic frequency response are becoming mandatory under modern grid interconnection standards, adding crucial resilience and value to the host network[89].

Table 1 Solar PV capacity factors by U.S. region

| Region | Annual CF (%) | Peak Month | Low Month | Installed Cost ($/W) |
| --- | --- | --- | --- | --- |
| Southwest (AZ, NM, NV) | 25–30% | June | December | $0.70–$0.90 |
| Southeast (FL, TX, GA) | 18–22% | May | December | $0.80–$1.05 |
| Midwest (IL, MN) | 15–19% | June | December | $0.80–$1.05 |
| Mid-Atlantic (NC, VA) | 17–20% | July | December | $0.85–$1.10 |
| Pacific Northwest (WA, OR) | 13–16% | July | December | $0.95–$1.20 |
| Northeast (NY, MA) | 14–17% | June | December | $0.95–$1.25 |

Figure 2 . Solar PV installed cost decline (2010-2026)

## 4.2. Solar Photovoltaic Systems

Wind energy contributes to a complementary generation profile to solar PV, as it is more productive during late-night and winter when solar PV is less industrious. In high resource areas, onshore wind turbines generally have capacity factors of 30-45%, and these are highest in areas like the U.S. Great Plains and in coastal areas which are influenced by offshore wind. The technology for generating power from offshore wind has come a long way and has reached a stage of maturity, where the capacity factor for fixed bottom installations is typically 40-55%, and for floating offshore wind, this is still in line with fixed bottom installations, with deployment to deeper waters underway. Onshore wind's levelized cost has also reduced significantly, now around $26-$50/MWh in recent analyses, making it one of the lowest cost generation sources in the world[90].

There have been improvements in wind resource assessment through the development of tools for measuring wind resources and atmospheric modeling. While ground-based anemometry is the standard for project-level assessment, the use of LiDAR systems is becoming common for remote wind profiling and wake characterization, providing flexible and cost-effective measurement capabilities. The use of numerical weather prediction (NWP) models and computational fluid dynamics (CFD) can now provide detailed flow characterization of wind over complex terrain. These models account for the loss of downstream turbine energy production due to turbine wake, which can reach 10–30% depending on spacing and atmospheric circumstances. The NREL Offshore Wind Market Report: 2024 Edition reports that the U.S. offshore wind project pipeline is nearly 80,000 MW (about 79.5 GW) in size, reflecting the scale of offshore wind installation in the country[91].

## 4.3. Hydroelectric Power

The dispatchability and ability to use hydro assets as generation and storage resources give it special attributes for data center integration. ROR (run of river) hydroelectric projects provide relatively stable baseload production, dependent on the flow variability for a particular season, and capacity factors are generally between 40-60%[43]. Reservoir based systems provide storage capacity from days to months and thus can provide firming capacity for variable renewables. The largest technology for grid-scale energy storage is pumped storage hydropower (PSH), which now makes up about 95% of installed storage worldwide and has a round-trip efficiency between 70-85%[44].

Hydro is not scalable for data center applications, primarily due to geographic constraints. The geomorphic conditions required for developing new PSH include a large vertical difference in elevation between the upper and lower reservoirs, the presence of a data center load center, and availability of water. New hydroelectric developments can take 5 to 10 years to obtain environmental permits, and the requirements are complex, covering impacts to aquatic ecosystems, recreational use, and recreational values[92]. But the current PSH facilities are an underutilized asset in data center integration, especially in areas with substantial capacity like the Appalachian Mountains (U.S.), the Alps (Europe), and the Scandinavian Peninsula.

## 4.4. Resource Assessment Methodlogies

Proper resource assessment is the backbone of economic success for renewable powered data centers. Solar irradiance data has been drawn from databases that are derived from satellite observations, including the Global Solar Atlas generated by the World Bank (WB), PVGIS [94] generated by European Commission Joint Research Centre (JRC), and ground-station measurements from networks like the National Solar Radiation Database (NSRDB) by NREL[93]. The standard input for energy yield simulations are datasets of typical meteorological year (TMY) data that are developed from multi-year historical records that are representative in a statistical sense. Typical uncertainty in energy yield predictions is 5% to 10% for well-characterized sites and 15% to 20% for sites with limited measurement data[94].

Geographic Information System (GIS) analysis is a powerful tool for site suitability assessment and can be used to evaluate a site based on a number of criteria including resource availability, proximity to the grid, land cost and availability, water availability for cooling, environmental constraints and construction accessibility[95]. These machine learning techniques have improved the GIS-based assessment by allowing for automated selection of the best sites from large geospatial datasets, potentially saving time and money in the preliminary feasibility studies[96].

## 4.5. Geographic Variability and Seasonal Patterns

It is important to appreciate the temporal variation of renewable resources when designing systems to satisfy reliability requirements. Solar generation fluctuates regularly on a diurnal and seasonal basis, typically peaking during the day (roughly between 6am and 6pm) and summer in temperate climates. Stochastic variability occurs on timescales of minutes to hours due to cloud cover, and the forecast errors on these timescales are generally between 5-10% mean absolute percentage error (MAPE)[97]. Wind generation has also been observed to have varying temporal characteristics, in most mid-latitude regions, wind energy tends to be higher at night and through the winter season, so as to complement solar energy. Figure 3, replicates the monthly wind-solar capacity factor complementarity during various months of the year[16], [87].

Figure 3 Monthly wind-solar capacity factor complementarity

The most common method to quantify wind-solar complementarity is by correlation analysis using the Spearman or Pearson correlation coefficient over various time scales (Hourly, Daily or Monthly). It was shown in various regions of Europe that the combined deployment of wind and solar power can benefit from cross-country coordination, which can improve the capacity factor of the combined plant by around 22% compared to a single plant deployment[98]. In data center applications, this redundancy gives direct benefit in terms of reduced storage space and system costs. Access to wind resources can lower the need for battery storage by 40-60% over solar-only deployments in a data center, based on complementarity at the specific site[99]. Climate change effects on renewable resources further increase uncertainty, including a range of small-scale changes in wind and solar resources that could influence long-term system planning as suggested in some studies[100].

5. Energy Storage and Backup Systems

Energy storage systems serve as the critical enabling technology for renewable-powered AI data centers, bridging the temporal gaps between variable renewable generation and constant computing loads. This chapter examines the sizing, selection, and integration of storage technologies, including lithium-ion batteries, long-duration storage alternatives, and conventional backup power systems.

## 5.1. Lithium-Ion Battery Systens

The cost of lithium-ion battery technology has dropped dramatically, changing the economics of integrating renewable energy. BloombergNEF has reported that the price of the batteries has declined over the past five years from $135 per kWh in 2020 to $115 per kWh in 2025, and in China, the price dropped below $65 per kWh at the cell level[17]. This trend is expected to persist, with the most recent cost estimates from NREL predicting $147 per kWh (low case), $243 per kWh (mid case), and $339 per kWh (high case) for 4-hour utility-scale systems by 2035[101]. A learning rate of about 19 percent for every doubling of cumulative production has been estimated for lithium-ion batteries, indicating further cost reductions with increased production[102].

The key factors of battery chemistry selection are cost, energy density, cycle life, safety and thermal management requirements. Due to its excellent safety (no thermal runaway risk), long cycle life of over 4,000 cycles at 80% depth of discharge, and its lower cost because it eliminates the use of cobalt and nickel, LFP (lithium iron phosphate) has become the predominant chemistry for stationary storage applications[45]. NMC chemistries provide higher energy density, lower cycle life, and higher safety concerns. Analysis shows that LFP is about 30 percent cheaper on a per-kWh basis compared to NMC for stationary use[46].

The round-trip efficiency of lithium-ion batteries varies from 85-95%, depending on the chemistry, cell design, and power conversion system. To ensure optimal cell temperature (usually 20-35 degrees Celsius) and to avoid accelerated degradation, thermal management is essential. Battery aging happens in two ways: calendar aging, which runs whether or not the battery is used, and cycle aging, which depends on how much charge or discharge the battery has experienced and at what rate[103]. Limiting the depth of discharge to 50% has been shown to approximately double cycle life, and, therefore, the use of larger systems than the nominal capacity requirements can enhance the overall battery system economics of their operation over time, despite the higher up-front capital costs[104].

## 5.2. Advanced Storage Technologies

One of the primary challenges associated with lithium-ion batteries is that they become cost prohibitive for extended periods of storage, which is where long-duration energy storage (LDES) technologies come into play. Vanadium redox flow batteries (VRFBs) have been developed with independent power and energy scaling, with cycle life of 20,000 cycles and very little degradation over time[47]. VRFB systems have already been commercially used at larger scales than 10MWh, and the main drawback is the relatively high initial cost, although costs are reducing as the scale of manufacturing increases.

Form Energy's iron-air battery is one of the technologies that could revolutionize ultra-long-duration storage. The technology employs a large amount of cheap materials (iron, water, air) to meet storage costs of $20 per kWh, whereas lithium-ion costing is targeted at $100 to $150 per kWh[48]. The data centre sector is interested in long-duration storage, the company having inked 12 GWh worth of multi-day iron-air batteries to new U.S. AI data centres[105]. Iron-air batteries have a round-trip efficiency of around 40% , below lithium-ion but acceptable given the possibility of lost renewable energy.

Hydrogen fuel cells and green hydrogen storage provide the widest range of storage durations – from weeks to months – enabling seasonal energy shifting that is not feasible with battery technologies. A hydrogen fuel cell back-up power system with a capacity of 3MW was demonstrated by Microsoft at its data center, running for 48+ hours using hydrogen fuel[106]. The round-trip efficiency of the hydrogen pathway, however, is about 30 to 40 percent, as opposed to 85-95% for lithium-ion batteries[49]. The economic viability of hydrogen relies on the ability to produce green hydrogen for $2/kg, versus the current production costs of $4 to $6/kg[107].

## 5.3. Energy Storage Sizing Methodology

There are three conflicting goals in sizing energy storage for renewable powered data centers – reliability (have enough energy to cover renewable energy gaps), cost (minimize capital and operations costs), and emissions (minimize renewable energy not used). There are three basic methods used: deterministic, probabilistic, and optimization-based.

The deterministic approach allocates storage to worst cases, e.g., the longest periods of low renewable generation. The worst case scenario for a data center in the U.S. Southwest location with on-site solar would be three consecutive overcast winter days, which equates to around 72 hours of battery storage at full load. This approach offers a firm guarantee of reliability, but usually leads to very large and expensive systems[50]. System reliability is quantified in the probabilistic approach using measures like Loss of Load Expectation (LOLE), which represents the average number of hours per year during which available generation is not adequate to meet demand. The LOLE of 0.1 hour per year, or 99.99 % availability, is a commonly used metric for mission-critical data centers[108]. This method gives a more in-depth view of reliability but involves in-depth time-series generation and load data.

The optimization-based approach constructs storage sizing as a mathematical programming problem to minimize the total system costs (capital expenditure plus operational expenditure throughout the project life cycle) while satisfying reliability constraints, carbon emission limits, and capacity constraints of the interconnection. Time-series dispatch simulation is a modeling approach that allows for detailed energy balance calculations at hourly or sub-hourly resolution for one or more representative years to assess system performance in a realistic operating environment.

Table 2 Storage duration options and trade-offs

| Duration | Technology | Cost ($/kWh) | Efficiency | Best Application |
| --- | --- | --- | --- | --- |
| 2–4 hours | Li-ion LFP | $75–$130 | 85–95% | Daily peak shaving & frequency regulation |
| 4–8 hours | Li-ion LFP | $110–$160 | 85–95% | Intra-day solar time-shifting |
| 8–24 hours | Flow Battery (VRFB) | $180–$350 | 65–80% | Multi-day firming & weak-grid support |
| 24–100 hours | Iron-Air | $20–$30 | 40–45% | Multi-day drought resilience & base load tracking |
| 100+ hours | Green $H_2$ Systems | $130–$220 | 30–41% | Seasonal shifting & long-duration backup |

## 5.4. Hybrid Backup Power Systems

Choosing a technology for back up power means balancing reliability, cost, emissions, and fuel logistics. Despite the declining economic viability of fossil fuels, and the drive to reduce carbon emissions, diesel generators are the most widely adopted backup solution, with capital costs between $300 to $600 per kW, a track record of reliability, and well-established fuel supply chains. Diesel generators do however generate substantial air pollutants (NOx, PM2.5) and CO2 emissions locally which poses conflicts with corporate sustainability objectives[109]. Typical diesel generator installations for a 100 MW data center with N+1 redundancy are about a total of 20 to 30 MW, with 24 to 72 hours of fuel storage to operate at full load.

Natural gas generators produce lower emissions than diesel. CO2 emissions are around 20-30% lower per kWh and local air quality impact is much lower. Capital costs are similar to diesel ($350 - $650/kW), but the reliability of fuel supply is dependent upon the natural gas pipeline infrastructure, which might be vulnerable during extreme weather events[110]. Microturbines, which are powered by natural gas or biogas, have lower efficiency (25-35%) than reciprocating engines and have smaller footprints and less maintenance[111].

Assessing grid connection as a backup method assumes that the utility grid is reliable, and has dual utility feeds from separate substations, minimizing the likelihood of a dual outage. Tiered power contracts are a mix of firm capacity and interruptible lower-powered rates that offer economic flexibility along with backup power[112]. Grid backup varies widely from region to region, with an average of 1.5 to 6 hours of utility outages per year in the U.S. for each utility and geographic area[113].

## 5.5. Integration and Control Architecture

In a microgrid for a data center powered by renewable energy, the energy management system (EMS) provides the central intelligence coordination of renewable generation, storage dispatch, backup power activation and demand-side management. The modern EMS platforms have three main levels of control: device-level controllers that react to the grid signals in milliseconds, facility-level EMS that control dispatch optimization every hour and corporate-level optimizers that control resource allocation across multiple facilities[114].

Model-predictive control (MPC) is the preferred dispatch optimization approach, which combines forecasting of renewable generation and load demand to provide 24 to 48 hour dispatch optimization, updated periodically[115]. The MPC formulation aims to minimise a cost function comprising energy procurement costs, battery degradation costs, demand charge penalties, and carbon emission costs, while satisfying physical constraints such as battery state-of-charge limits, inverter capacity ratings, and interconnection power flow bounds. Research has shown that MPC-based dispatch can provide savings of 10-20% in energy cost, while achieving similar or better reliability performance, over simple rule-based dispatch strategies[116].

A key aspect of system reliability is implementing fault detection, redundancy, and failover logic. Modern EMS platforms have N+1 or 2N redundancy for key components and automatically fail over if any controller or communication fails. To address the growing threats to critical infrastructure, cybersecurity provisions, such as encrypted communications, multi-factor authentication and network segmentation between operational technology (OT) and enterprise IT networks, are vital[117].

6. Power System Modeling and Simulation

This chapter examines the tools, methodologies, and validation approaches for designing and analyzing hybrid microgrid systems for renewable-powered AI data centers. Accurate modeling is essential for predicting system performance under varying operating conditions, optimizing component sizing, and validating control strategies before deployment.

## 6.1. Steady-State Power Flow Analysis

The voltage profile, power flow, and losses derived from steady-state power flow analysis are the basis for the design of electrical systems, as they define equipment ratings and protection settings. The power flow equations are nonlinear, and the Newton-Raphson method is the standard algorithm used to solve them, needing usually 4 to 8 iterations to converge for well-conditioned system[118]. The DC power flow approximation also includes a linearization of the AC power flow equations, omitting reactive power and voltage magnitude changes, and leads to computationally efficient results appropriate for screening level analysis and large-scale system studies[119].

Optimal power flow (OPF) is an extension of the basic power flow formulation with an objective function (typically cost minimization or loss minimization) and operational constraints on voltage magnitudes, line flows, and generator outputs. OPF can be employed in renewable powered data centres to optimise the dispatch of renewable generators, battery storage and grid interconnection to minimise energy costs whilst maintaining power quality and reliability[120]. In contingency analysis, which is based on the N-1 reliability criterion, the performance of a system is tested when one component fails, to ensure that the system will still be able to operate satisfactorily after this failure[121]. Often used tools for power flow analysis are MATPOWER, which is an open-source MATLAB toolbox; PSS/E, a commercial tool; and DIgSILENT PowerFactory, a commercial and popular tool in Europe[122].

## 6.2. Transient Stability and Grid Dynamics

Transient stability analysis involves studying the transient dynamic response of the power system after a large fault, generator trip, or sudden load change. Transient stability is also an important issue for microgrids in data centers with high renewable penetration, due to the lack of inherent rotational inertia in inverter-based resources. Virtual inertia can be achieved by grid-forming inverters, where the reference voltage and frequency are generated by the inverter without using a grid synchronizing signal, by controlling their dynamic response, as that of a synchronous machine[18], [123]. The transition from on-grid to off-grid (islanded operation) is a significant transient event that occurs when the utility grid suffers a disturbance, and for which careful design of inverter control parameters, protection settings, and load shedding schemes is required[124].

The challenge of PLL stability arises as renewable penetration increases. However, PLL-based grid-following inverters can suffer from oscillatory operation or complete loss of synchronization in weak grid condition, when the short circuit ratio (SCR) at the point of interconnection is low, which can cause cascading failures[125]. There are several well-documented examples of the occurrence of sub-synchronous resonance (SSR) phenomenon between inverter controls and series-compensated (SC) transmission lines, and these interactions require detailed electromagnetic transient (EMT) simulation studies for grid-connected renewable plants[126].

## 6.3. Harmonic Analysis and Power Quality

Harmonic analysis is crucial to ensure compliance with power quality standards set in IEEE 519 and to help develop the correct mitigation. The harmonic profile of a data center microgrid depends on the combined effect of all the data center nonlinear loads such as IT equipment SMPSs, cooling system VFDs, LED lights, and the harmonic currents produced by the renewable inverter[22]. Frequency-domain analysis techniques such as Fourier decomposition and harmonic impedance scanning are employed to detect resonance conditions which could increase the level of specific harmonic orders[127].

Passive filters (tuned LC circuits), active power filters (APFs), multi-pulse rectifier configurations, and advanced inverter control algorithms to reduce harmonic current injection are all options for harmonic mitigation[127]. The choice of mitigation technology will be a function of the harmonic spectrum, dynamics of loading and cost considerations. Active filters tend to be the preferred choice for AI data centers where the loads are often irregular, as they can continuously adapt to shifts in the harmonic profile[128].

## 6.4. Microgrid Modeling Frameworks

There are a variety of software packages for micro-grid modeling and simulation, ranging in fidelity and in efficiency. HOMER (Hybrid Optimization Model for Electric Renewables), developed by NREL and maintained by UL Solutions, is a dispatch simulation that combines economic optimization and is particularly useful for sizing applications and comparison of technologies[129]. HOMER Pro has built-in component models of solar PV, wind turbines, batteries, generators, and grid interconnection and sensitivity analysis to explore parameter uncertainty. HOMER's hourly time resolution, however, might not be adequate for sub-hourly phenomena like frequency regulation and voltage transients.

For detailed electromagnetic transient simulation, MATLAB Simulink with the Simscape Electrical toolbox delivers analysis of the dynamics of inverter control, protection system co-ordination and fast-switching power electronics. There are several open-source tools available such as Pandapower (Python power flow), PyPower (MATLAB POWERWORLD port to Python), and OpenModelica (equation-based modeling) for research and preliminary engineering studies[130]. The choice of the modeling framework should be determined by the analysis needs: HOMER for system sizing and economic optimization, MATLAB/ETAP for detailed electrical design and protection coordination, and PSCAD/EMTDC for electromagnetic transient studies of inverter dominated systems[131].

## 6.5. Time-Series Simulation and Forecasting

To assess renewable energy based data center systems under realistic operating conditions, time-series simulation at hourly or sub-hourly resolution is crucial. Hourly simulation accounts for the diurnal and seasonal variation in renewable generation and load demand, and it can be used to provide the energy balance calculations required to determine the storage capacity required, energy demand and supply from the grid, and energy balance metrics for system reliability[132]. At 5 to 15 minute resolution, sub-hourly simulation can capture the rapid transients from cloud transients, wind gusts and load steps, which impact on power quality and frequency regulation.

Stochastic simulation methods, especially Monte Carlo methods, can be used to quantify uncertainty in the performance of a system, resulting from errors in forecasts, equipment failures and climate variability. Monte Carlo analysis runs thousands of simulation runs, with the input parameters randomly sampled across the range, which generates a probability distribution of key output metrics like annual energy cost, LOLE and renewable utilization fraction[133]. Forecast integration is essential for model-predictive control strategies and for day-ahead dispatch planning a prediction horizon of 6 to 48 hours for solar and wind is needed. The accuracy of these forecasts directly impacts the performance of optimization-based dispatch, with day-ahead solar forecast errors of 10-15% MAPE and intra-day errors of 5-10% MAPE being typical of state-of-the-art systems[134].

## 6.6. Machine Learning for Control and Forecasting

Machine learning techniques are increasingly being applied to both forecasting and control functions in renewable energy systems. Recent studies have shown that neural network architectures such as Long Short-Term Memory (LSTM) networks, Convolutional Neural Networks (CNN), and attention-based Transformer models can enhance the accuracy of solar and wind power forecasts by 15-25% over traditional numerical weather prediction techniques[135]. Deep reinforcement learning (DRL) has been proposed as a viable method to optimize dispatching policies for controlling a microgrid, in which an agent learns from an interaction with a simulated environment to find the optimal dispatching policy[136].

Digital twin concepts, which involve virtual copies of physical systems that are continuously updated with sensor data, can facilitate predictive control strategies that can anticipate and proactively adjust to varying conditions. A digital twin of a data centre microgrid can simulate the effect of the renewable generation prediction on battery dispatch, define the most suitable load scheduling periods and predict equipment degradation[137]. There are still difficulties with ensuring the generalizability of machine learning models beyond the boundaries of the training data, especially for edge cases and extreme weather conditions that may have been underrepresented in the historical datasets[138].

7. Framework for Renewable-Powered AI Data Centers

This chapter presents the core contribution of this paper: a comprehensive, seven-component framework for designing, deploying, and operating AI data centers powered predominantly by renewable energy. The framework integrates site assessment, technology selection, electrical integration, control strategy, workload flexibility, economic viability, and sustainability compliance into a unified decision-making methodology.

## 7.1. Machine Learning for Control and Forecasting

The framework consists of seven interrelated elements that cover key aspects of renewable-based data center design and operation. These components are not separate, but rather are interdependent, with decisions made in one component affecting and limiting choices in another component. The framework has been designed to be modular and scalable, and can be adapted to fit facilities from the small edge computing node (1-10 MW) to the hyperscale cloud data center (100+ MW) located in different geographic and climatic conditions.

[Figure: fig7_1.png - not found]

Fig. 5. Introduced a seven-component framework architecture for AI data centres using renewables.

Site Assessment (Component 1) covers renewable resource availability, grid interconnection feasibility, water and land availability, and climate resilience. Component 2 is called Technology Selection and covers optimizing the renewable capacity, storage time and backup power type according to site-specific conditions. Component 3, Electrical Integration, specifies the voltage ranges, topology, redundancy and power quality mitigation. Control Strategy relates to dispatch algorithms, forecasting integration and demand response mechanisms (component 4). Workload Flexibility (component 5) measures the extent to which load can be shifted, deferred, or prioritized. The financial performance is modeled in Component 6, Economic Viability, using LCOE, NPV, and IRR analysis. Component 7: Resilience and Sustainability focuses on reliability measures, carbon footprinting, and regulatory adherence.

The three main quantitative goals of the framework are: (1) cost of delivered energy (dollar per Megawatt-hour, $/MWh), (2) system reliability (percent uptime, >99.99 percent), and (3) carbon emissions (gCO2 per kWh). The objectives are also frequently conflicting and must be balanced by means of multi-objective optimization techniques. The main variables are the capacity factor of renewables, the duration of storage (in hours), the type of back-up power, interconnection capacity of the grid, and flexibility parameters of the demand.

## 7.2. Site Selection and Resourc Assessment

Site selection utilizes a multi-criteria decision analysis (MCDA) approach that assigns weights to a series of criteria related to resource quality, infrastructure access, environmental factors, and economic considerations, then scores candidate locations based upon the weights of the criteria. The quality of the solar resource is evaluated by the annual capacity factor target exceeding 20 percent, based on satellite data corrected for local terrain shading and typical meteorological conditions. For onshore installations, the wind resource targets a capacity factor above 25 per cent, derived from measurements taken on meteorological towers or from LiDAR, for at least one year [94].

Interconnection feasibility is also an important criterion for site selection; this will influence project viability due to the cost and time of interconnection. Interconnection costs are typically $500,000 to $2 million for sites within 5 km of existing transmission infrastructure with available capacity and $5 to $10 million when new transmission line construction is necessary [23]. Climate resilience assessment quantifies the likelihood of extreme events such as hurricanes, flooding, wildfires, and ice storms occurring that may harm renewable generation equipment, affect grid supply, or affect the performance of cooling systems[139]. In areas of the world that have a high climate risk, extra engineering interventions such as the installation of raised equipment platforms, strengthened structural ratings or redundancy upgrades may be needed, adding to capital expenses.

## 7.3. Technology Mix Optimization

The technology mix optimization is a problem that balances the mix of renewable generation, storage duration, and backup power type to minimize the total cost of the system over the expected project lifetime of 20–25 years, while also meeting reliability and emissions targets[51]. The three primary choices used as critical decision variables for this optimization are the renewable capacity expressed as a percentage of the mean load (100% or 110% or 150% of mean load or higher), storage duration scaled across 4, 8, 12, or 24 hours, and backup power technology: diesel generator, hydrogen fuel cell, grid connection, or hybrid configuration.

Visually depicted in Fig. 6. Cost-emissions Pareto frontier for technology mix optimization, this modelling quantifies trade-offs needed to reconcile the economics of the system with the performance of the set of environmental targets. Parametric sensitivity analysis shows that this optimal technology mix is most sensitive to three main parameters: (1) renewable capacity factor, with an error of 5% leading to an approximate 15%  change in the LCOE; (2) battery storage cost, where a $20 per MWh change in the battery storage cost results in an approximate 10% change in LCOE; and (3) grid electricity price, where a 20$ per MWh increase in the grid electricity price has a significant impact on the solution and leads to a higher renewable penetration. Combining these factors, the analysis shows that hybrid systems are by far the most cost-effective in most cases. Systems with 100% to 150% renewable generation and 4 to 8 hours of battery storage and dedicated grid backup reliably achieve a highly competitive LCOE of 35$ to 80$ per MWh reliably satisfying a 99.9% system reliability target[140].

## 7.4. Electrical Architecture and Integration

The Electrical Architecture specifies the voltage levels, distribution topology and integration points of all the generation, storage and load elements. The selection of primary interconnection voltage is a compromise between equipment cost and power transfer capacity, with higher voltage levels (25 kV vs. 13.8 kV) also decreasing conductor size and losses, but increasing equipment cost and the required rating of switchgear and protection devices[65]. A primary interconnection of 25 kV is generally the most economical option for a 100 MW data center, and step-down to 13.8 kV is more economical for facility distribution, while further step-down to 480 V is more economical for equipment power distribution.

A discussion about the debate between DC and AC distribution for data centers is worth considering. While AC-DC-AC conversion in the UPS is a double conversion loss, the conversion from AC to DC and back to AC (AC-DC-AC) can be avoided by using DC distribution, which can boost efficiency by 3 - 5 percent, but involves the use of DC-rated switchgear, circuit protection, and building wiring, which are more expensive and less readily available[141]. In AI data centers with a high level of renewable energy consumption, where most of the energy is likely to be sourced from inverter-based DC power, DC distribution systems can present attractive efficiency benefits that outweigh the additional cost of the equipment.

## 7.5. Control and Dispatch Strategies

Control strategy is the method by which the data center can coordinate renewable generation, storage, backup power, and demand-side resources to reliably and economically meet the demand for power. The proposed framework adopts a hierarchical control structure with three different layers and each with different time scale and different control purpose.

Fig. 7. Hierarchical control architecture for operation of a data center micro grid.

The device-level control (level 1) controls the grid-forming or grid-following characteristics of the inverter, reacts to frequency and voltage deviations, and offers fast frequency response at millisecond timescales. At the facility-level (Level 2), EMS operates at minute to hourly timescales, and performs dispatch optimization using model-predictive control with 24-48 hour forecast horizons[142]. At level 3, the corporate level, the optimization is conducted at the hourly to daily time scale and involves the scheduling of multiple facilities, such as routing compute workloads to facilities that offer the best renewable conditions[142].

AI workload scheduling is a special type of demand-side resource that data centers have that the traditional electricity consumers. Training workloads, which can stand hours to days of delay without compromising service quality, can be planned to coincide with times of high renewable generation. Relaxed latency requirements for inference workloads can be spread across facilities or time-shifted within SLA limits. Energy savings of up to 10% to 20% and reductions in carbon emissions of 5% to 15% are shown by quantified benefits from industry deployments, which shows that workload scheduling alone can make a difference[143].

## 7.6. Demand-Side Management and Load Flexibility

Data center workloads are divided into one of four flexibility classes: (1) Training, highly flexible with deferral windows of hours to days, (2) Inference, less than 100 ms response time to some deferral, depending on application, (3) Analytics and Batch processing, highly flexible and easily shifted to renewable peaks, and (4) Background tasks, such as model optimization, data indexing, and system maintenance, are fully interruptible [144]. This classification allows the control system to dynamically prioritize and schedule workloads according to forecasts of renewable availability.

Workload scheduling requires changes to the job scheduling infrastructure, which are executed through Kubernetes extensions or custom scheduling plugin that calls a renewable availability API that provides 24-48 hour forecasts[145]. The API provides time-series data on the percentage of the total load to be met from renewable generation, which the scheduler can use to determine good time periods for workloads that can be deferred. SLA relaxation parameters are the maximum allowable increase in latency (usually 5-10%) that a business can expect in return for the cost and carbon savings of more than 15%.

## 7.7. Cooling System Coordination

The concept of cooling system coordination is based on synchronizing the electric and thermal energy systems to optimize overall efficiency. Thermal energy storage (TES) systems, particularly ice storage and chilled water storage, enable cooling demand to be shifted to periods of abundant renewable energy or low electricity prices. If there is excess renewable energy during periods of high renewable energy, it can be utilized to generate chilled water or ice, and then stored for use during other times of low renewable energy production[79]. Dynamic setpoint management enables the cooling system temperature to vary within a control range, thereby saving energy when renewable energy sources are available and strengthening control when the grid becomes critical[146].

The efficiency benefit of liquid cooling for AI accelerators is impressive, with cooling energy per watt of IT load dropping from 0.3W to 0.5W (air cooling) to 0.1W to 0.2W (direct-to-chip liquid cooling)[34]. Waste heat recovery involves recovering the thermal energy that the data center rejects for other applications, like district heating, greenhouse heating, or industrial process heat, in order to reduce the overall amount of energy consumed by the data center, with a benefit of 5-10% of total energy costs[147].

## 7.8. Economic Model and Financial Vaibility

The economic model employs standard financial metrics including Levelized Cost of Energy (LCOE), Net Present Value (NPV), Internal Rate of Return (IRR), and payback period to evaluate the financial performance of renewable-powered data center configurations. The LCOE calculation aggregates all capital and operating costs over the project lifetime and divides by total energy delivered, discounted to present value[148].

Table 3 CAPEX Breakdown by Technology (2025–2026)

| Technology | CAPEX Range | Fixed O&M (%/yr) | LCOE ($/MWh) | Lifetime |
| --- | --- | --- | --- | --- |
| Solar PV (Utility) | $900–$1,600 /kW | 0.4–0.8% | $50–$80 | 25–30 years |
| Wind Onshore | $1,800–$2,600 /kW | 1.5–2.5% | $45–$70 | 20–25 years |
| Li-ion Battery (4h BESS) | $180–$320 /kWh | 1.0–2.0% | $80–$130 | 15–20 years |
| Diesel Generator | $400–$750 /kW | 2.0–3.5% | Fuel dependent | 20–25 years |
| H2 Fuel Cell | $1,600–$3,200 /kW | 3.0–5.0% | $140–$220 | 12–15 years |
| Grid Electricity | N/A | N/A | $85–$160 | N/A |

The U.S. Inflation Reduction Act (IRA) and the subsequent extensions into 2025 and 2026 offer substantial financial benefits which dramatically enhance project economics. For solar, energy storage systems (BESS), and qualifying hydrogen production equipment, the Investment Tax Credit (ITC) of 30 percent baseline of eligible project costs effectively decreases capital expenditure by about 30 percent[149]. The ITC can be combined with domestic content bonuses, energy community stackability, and accelerated depreciation under MACRS (5-year recovery for solar and battery storage, 7-year for wind), which can boost the effective ITC to 40 to 50 percent of total project cost.

By applying an improved discount rate of 7.5% (due to the sustained higher macroeconomic interest rate) and central cost estimates, payback periods for hybrid renewable systems using stacked ITCs range from 4 to 8 years, while without federal incentives, payback periods are between 9 and 16 years[150].

## 7.9. Reliability and Resilience Metrics

The framework sets reliability objectives consistent with the worth of AI computing workloads. Availability is the main reliability metric, representing the percentage of time that the system provides adequate power to keep all critical computing functions running. Target availability is 99.99% or 52.6 minutes per year[151]. A complementary metric that quantifies the expected frequency of insufficient "generation events" is Loss of Load Expectation (LOLE), which is measured in hours per year. A data center aiming for 99.99% availability would expect to experience around 0.1 hours of LOLE per year.

Energy resilience represents the period of time (typically in hours) the facility can sustain its operations during a full grid outage using stored energy, and is crucial to disaster preparedness. If normal load conditions are used, a data center with 8h of battery storage and 72h of diesel fuel can operate for more than 80h if the power grid fails[152]. The N-1 contingency criterion states that if any one component, such as a generator, a battery string or a grid feed is lost, then the system is still reliable.

## 7.10. Carbon Accounting and Sustainability

The framework covers the full scope of the Greenhouse Gas Protocol. Scope 1 emissions include direct emissions from burning fuel in backup generators and fuel cells, usually making up less than 1% of the total emissions from a facility with low usage of its back-up generators[153]. The largest are Scope 2 emissions, purchased electricity, and they are the first to be reduced by purchasing renewables. These are known as scope 3 emissions, representing around 5 to 10 grams of CO2 per kWh over the asset's lifetime and can be mitigated by implementing circular economy approaches, such as embodied carbon in equipment manufacturing or end-of-life disposal, respectively[154].

The 24/7 Carbon-Free Energy (CFE) standard, which calls for matching carbon-free generation time to electricity consumption time, is considered the most stringent sustainability measure and is being embraced by many of the industry's largest operators, such as Google and Microsoft[6]. 24/7 CFE will require the implementation of sophisticated forecasts and control systems that can optimise energy dispatch every hour, along with clear procurement of time-matched renewable energy via PPAs or on-site generation. The framework suggests that annual renewable energy matching should be implemented first, followed by hourly matching when the control systems and the market mechanisms are advanced.

8. Case Studies: Real-World Deployments

This chapter examines the renewable energy strategies of five leading technology companies, extracting lessons learned and validating the proposed framework against real-world implementations. Each case study provides detailed technical specifications, performance metrics, financial data, and strategic insights.

## 8.1. Google Data Centers: Renewable Energy Matching

Google has over 100 data center facilities worldwide and has set the most aggressive renewable energy goal in the technology industry: 24/7 carbon-free energy (CFE) for all local data center electricity grids where it operates by 2030. Google's aggressive purchasing approach has resulted in a growing clean energy portfolio, with the company now having over 22 GW of total renewable energy contracts through a global portfolio of more than 170 power purchase agreements (PPAs) that include utility-scale solar power, onshore wind, geothermal, and battery storage solutions. Driven by the growing computational workload of the generative AI age, Google met an important milestone in its operations, raising the hourly 24/7 CFE score for its entire facilities global footprint to 66 percent, while 9 of 20 primary data center grid regions achieved an 80 percent, hourly CFE score [55].

A number of key technical installations are in place and marked as part of this infrastructure strategy, such as the 50 MW on-site wind generation array at the Council Bluffs facility in Iowa that directly connects with the data center's electrical distribution system and exports excess peak capacity back to the regional transmission organization. Likewise, a portfolios of wind and solar combined PPA power plants greater than 200 MW installed in Chile's Atacama Desert takes advantage of complementary resource timing patterns, as the wind is found to occur in times of low solar irradiance, and the solar resource is found to occur in times of high wind speed in the localized thermal wind zones. Modern infrastructure blueprints for AI workloads in the modern era of Gemini place a strong emphasis on deep grid integration and spatial load shaping. This includes specialized, direct backlinks with utility scale battery storage networks to enable facilities to shift flexible server demand from high-carbon time periods to when there is high local renewable generation[55].

Structured corporate PPAs have reliably proven their ability to protect against short-term fluctuations in wholesale grid electricity markets for 15-25 year contracts and energy cost metrics ranging from $30 to $50 per MWh – values that are more predictable than the $70-120 per MWh that can be found across main commercial markets [55] – across the board. The company's focus on geographic distribution and its use of carbon-aware software scheduling allows it to dynamically place non-interactive compute workloads to facilities that are in the best condition for generating clean energy. This distributed computing approach is a basic solution that eliminates the penalties associated with local over-provisioning in physical facilities and chemical storage that would otherwise burden individual facilities. Concrete industry validation for strict site assessment, multi-technology resource aggregation, carbon-aware control strategies, and long term economic viability is provided by framework validation, which correlates Google's active portfolio to Components 1, 2, 4 and 6 of the proposed architecture.

## 8.2. Meta: Fuel Cell Integration at Prinveille

Meta (Facebook) has been following a unique path with its focus on fuel cell technology in its Prineville, OR data center campus. It has 5 MW of Bloom Energy solid oxide fuel cells (SOFCs) using natural gas as the main onsite generation resource, 1 MW of onsite solar canopy generation, and 50 MW of contracted wind energy through PPAs[57]. When used as combined heat and power (CHP) systems, the fuel cells' electrical efficiency is about 60% and the waste heat is recovered for building heating, yielding overall CHP efficiency of more than 80%[57].

Performance metrics show a facility PUE of ~1.10, one of the lowest in the industry, and fuel cell up time in the high 90's percent. But there are some problems that have arisen. The cost of replacing fuel cell stacks ($1 to $3 million every 5 to 8 years) is a large operating cost and the use of the natural gas feedstock introduces a pathway for carbon emissions that is incompatible with net zero commitments[155]. One of the factors with which Meta is working on decarbonizing its fuel usage is to shift from natural gas to green hydrogen as its fuel source, but it is unclear when this shift will happen or if it will be a costly process due to the lack of hydrogen production and distribution infrastructure. Fuel cells are shown to be a suitable bridge technology (Component 2: Technology Selection) but not necessarily the future preferred solution as battery storage costs are decreasing.

## 8.3. Microsoft: Modular Design and Nuclear Partnership

Microsoft has been looking at two innovative solutions for sustainable data center infrastructure: the experimental Project Natick which is an underwater data center, and baseload power supply with nuclear energy. The 99.9% reliability of Project Natick Phase 2, which was deployed off the coast of Scotland, was attributed to the less corrosive environment of the water and the nitrogen-filled sealed container preventing humidity-induced failures, and the results showed an eight-fold reduction in failure rates when compared with facilities of similar capacity on land[60].

The most sizeable corporate nuclear energy pledge so far from Microsoft is a partnership to restart the Three Mile Island Unit 1 reactor (Crane Clean Energy Center) to supply 835 MW of baseload energy for its artificial intelligence operations[59]. Also, Microsoft has backed Helion Energy, a fusion energy start-up with the goal of making it commercially viable by 2028 and has signed a deal to buy electricity generated by fusion[156]. A second option for this nuclear integration with data centers is small modular reactors (SMRs), which can range in size from 50 to 300 MW, and are not expected to be commercialized until the 2020s or beyond. Framework alignment: Microsoft's approach is aligned with and validates Component 7 (Resilience and Sustainability), and shows how next generation technologies will augment renewable energy systems.

## 8.4 Equinix: Distributed Solar PPAs:

As a global provider of more than 260 data centers in 33 countries, Equinix has taken a multi-location approach to renewable procurement, based on the geographic distribution of its locations. The company has signed more than 350 MW of solar and wind power through PPAs in California, Arizona, Texas, the Midwest U.S. and several European countries. Equinix has also published a sustainability report for 2024, which shows that 96 percent of its global portfolio is covered by renewable energy, and that Equinix will reach 100 percent by 2030[62].

The financial model shows that PPA pricing in the markets at $40 to $60 per MWh, based on long-term (15 to 20 year) contracts, is lower than historical grid rates in most Equinix markets, which yields cost savings and price stability. The company's multi-facility load balancing enables routing of customer workloads to facilities with different renewable profiles, allowing for a virtual power plant that helps to balance the aggregate renewable variability. Yet, there are barriers to be faced in the part of the world where access to PPA is poor and in the markets where the cost of connecting to the grid is high compared to the savings from electricity. The distributed approach employed by Equinix is found to be a good solution to the two components – Workload Flexibility and Economic Viability – on validation of the framework.

## 8.5 Apple:100 Percent Renewable Commitment

Apple has now made a full 100% commitment to renewable energy powering all of its global operations, including data centres, corporate buildings and retail stores, as well as its manufacturing supply chain. The Maiden, North Carolina data center is a flagship facility, using 10 MW of Bloom Energy fuel cells, and a 100-acre solar array producing around 42 million kWh per year on site. Apple's strategy includes owned generation on site (where possible), long-term PPAs and renewable energy certificates to meet its goals[64].

The price difference for a 100% renewable power mix is estimated at 10-20% higher than using conventional grid electricity, although Apple says efficiencies from self-generated power and from the grid via revenue streams mitigate this cost [64]. Some of the main issues are high capital costs of building owned generation, supply chain limitations with renewable equipment and saturated PPA markets in certain areas. The staged, portfolio approach is a lesson learned in the Apple story that reinforces Component 7 (Sustainability) and underscores the need for long-term strategic planning to meet comprehensive renewable energy goals.

## 8.6 Comparative Analysis

Table 4 Comparative analysis of industry case studies

| Organization | Approach | Renewable % | Storage | Backup | Est. LCOE |
| --- | --- | --- | --- | --- | --- |
| Google | PPAs + Load Shift | >64% hourly | Grid-scale BESS | Grid | $40-60/MWh |
| Meta | Hybrid Fuel Cell | ~100% (annual) | Fuel Cell | Nat Gas | $50-80/MWh |
| Microsoft | Modular + Nuclear | TBD | Nuclear (future) | Grid | TBD |
| Equinix | Distributed PPAs | 96% (global) | Minimal | Grid | $35-60/MWh |
| Apple | Owned + PPAs | 100% (annual) | On-site solar | Rare | $60-90/MWh |

Common success factors identified across all five case studies include: (1) long-term renewable procurement through PPAs or owned generation, providing price stability and supply certainty; (2) geographic diversification of data center capacity across regions with complementary renewable resources; (3) active engagement in workload flexibility and load shifting to maximize renewable utilization; (4) proactive regulatory engagement to shape supportive policy environments; and (5) investment in proprietary technology and control systems that enable sophisticated energy management. These factors collectively validate the multi-component approach proposed in this paper's framework.

9. Technical Challenges and Solutions

This chapter provides a detailed examination of the principal technical barriers to high-renewable-penetration data center operation and presents state-of-the-art mitigation strategies. Each challenge is analyzed with respect to its physical basis, impact on system design and operation, and available or emerging solutions.

## 9.1 Intermittency and Predictability

Solar and wind power are intermittent, and this intermittency can be seen on various timescales ranging from transients on the timescale of seconds or minutes, to a seasonal fluctuation in the resource. The high errors in day-ahead forecasts (10-15% MAPE) and intra-hour forecasts (5-10% MAPE) introduce uncertainty in dispatch planning that must be addressed through the use of storage, demand response, and grid interconnection[134]. The storage duration needed to meet typical shortfalls in renewables varies with the resource profile, with solar-only systems needing 4 to 8 hours of storage to meet evening peak requirements, and wind dominated systems in regions with 24 to 72 hours of storage lulls needing 24 to 72 hours of storage[76].

The use of geographic diversity in dispersed facilities offers a strong tool for minimizing overall variability. Spatial smoothing from facilities with distances greater than 500 km can lower the coefficient of variation of combined renewable energy generation by 40 to 60% when compared to a single-site deployment[98]. For multi-facility operators, this natural smoothing effect will lessen the need for per-facility storage and allow for more efficient use of common grid interconnection capacity. The use of advanced forecasting techniques such as ensemble numerical weather prediction and cloud tracking using satellites has further enhanced the predictability of weather events, with machine learning post-processing reducing the MAPE by up to 15-25%[157].

## 9.2 Grid Stability and Frequency Control

Synchronous generators are being replaced by inverter-based resources, which diminishes the natural inertia that helps regulate grid frequency when disturbances happen, making it more difficult to keep the frequency within acceptable limits. With high levels of renewable generation (above 50%) the rate of change of frequency (RoCoF) after a generator trip or load change may be beyond traditional governor-based frequency response, which can lead to load shedding or cascading events. The response time of grid-forming inverters is milliseconds, as opposed to seconds, making them more responsive to the effects of inertia than synchronous machines, and can be achieved using control algorithms which replicate the inertial reaction of a synchronous machine[18].

Weak grid conditions, where short circuit ratio at the point of interconnection is low, also pose stability issues. In such cases, the voltage at the point of interconnection is significantly affected by the output of the renewable plant, and grid-following inverters with PLL control can display instability or oscillatory operation. These solutions involve deployment of grid-forming inverters, synchronous condensers (rotating masses without generation capacity) that provide inertia and reactive power support, STATCOM devices for dynamic voltage regulation, and fast frequency response of battery systems that can inject or absorb power in sub-second time [158].

## 9.3 Power quality and Harmonic Distortion

Data center loads contribute harmonics in several ways: SMPSs consume non-sinusoidal current that includes harmonics of the third, fifth and seventh order; VFDs that are used for cooling systems introduce harmonics related to their switching frequency; and renewable inverters with pulse-width modulation (PWM) switching create harmonics linked to their switching patterns. The cumulative impact of many individual loads can cause THD to be greater than the IEEE 519 standard of 5% at the POC, especially when the load is light and the harmonic currents are significant portions of the total current[54].

Active power filters (APFs) continuously monitor harmonic currents and feed the compensating currents into the system, resulting in a reduction of THD down to less than 3%; Multi-pulse rectifiers (12-pulse, 18-pulse or 24-pulse) are a natural solution for cancellation of low-order harmonics through phase-shifting transformer configurations; Passive LC filters tuned to the harmonic frequencies are other solutions which are available. In the case of renewable powered data centers, a combination of inverter harmonics and load harmonics requires system-level analysis using harmonic impedance scanning and frequency domain simulation to determine the resonance conditions that may amplify harmonics of interest[127].

## 9.4 Grid Interconnection Complexity

Grid interconnection is still one of the biggest hurdles to the deployment of renewable energy at the scale of data centers. Interconnection queues have increased significantly in crowded grid areas; for example, the interconnection queue at CAISO has grown to over 2,000 projects representing more than 1,000 GW of proposed capacity, and the interconnection queue at PJM has grown to more than 3,000 projects. The general interconnection timeline is 2 to 4 years and involves feasibility study (3 to 6 months), system impact study (6 to 12 months), facilities study (6 to 12 months), and construction (12 to 24 months). Project costs may vary from $50,000 for simple distribution level interconnections to $500,000 or more for projects involving distribution or transmission level grid upgrades[24].

FERC Order 2023, issued in July 2023, is designed to resolve interconnection delays in several ways, including: setting a uniform timeframe for the completion of studies (180 days for cluster studies); identifying pre-certified equipment categories that would be exempt from detailed individual studies; and making changes to how the costs of upgrades are shared, moving shared upgrade costs to the requesting parties[159]. IEEE 1547-2018 provides technical requirements for interconnection of distributed energy resources (DERs), such as anti-islanding protection, voltage and frequency ride-through, and power quality limits, while IEEE 2800-2022 specifies the performance requirements for larger inverter-based distributed energy resources (IBDERs) at transmission voltage levels[53].

## 9.5 Demand-side Management and AI Workload Flexibility

AI workload flexibility is a distinct and growing demand-side resource, and it can have the potential to substantially decrease the cost and complexity of integrating renewable energy. Training workloads (often hours to weeks to complete, not latency-sensitive) can be deferred to times of low latency demand and high renewable generation[145]. Deferral windows of hours to days make batch processing workloads such as data preprocessing, model validation, and analytics even more flexible. Time-shift can be used for inference workloads that do not need to have a high latency requirement, like batch image inference or non-interactive recommendations, within SLA.

Energy cost reduction of 10-20% through time-of-use rate optimization and carbon reduction of 5- 15% through increased use of on-site renewable generation are indicated by quantified benefits from industry deployments and simulation studies[160]. It requires integration between the workload scheduler (usually Kubernetes-based) and the energy management system, and the renewable availability API delivers 24-to-48-hour forecasts of renewable generation as a portion of total load [145]. Some of the major considerations are that the deferral may lead to an increase in latency as experienced by users, the risk of violating SLAs if deferral is performed too aggressively, and the operational complexity of coordinating workload scheduling across multiple facilities and time zones.

## 9.6 Energy Storage Control and Battery Management

There are several criteria for optimal battery dispatch: most renewables usage, least energy cost, longest battery life, and sufficient reserve for emergency backup. The state of charge (SOC) setpoint optimization defines the charging and discharging timing according to current state and future forecasting, where the most advanced approach is model-predictive control (MPC)[115]. The economic factor of battery ageing: deep cycling (depth of discharge above 80%) decreases battery life, while shallow cycling increases battery life, but at the cost of reduced energy capacity for renewable time-shift. Studies have shown that maximum depth of discharge of 50% can nearly double cycle life, indicating that appropriately oversizing battery systems may provide better lifetime economics, albeit at higher initial capital cost[104].

Dual-use battery strategies can enhance financial return on battery investment by enabling both renewable integration and grid services (frequency regulation, capacity markets, ancillary services). The estimated revenue from a 100 MW data center with 10 MW of available battery capacity for frequency regulation is approximately $3 million per year at PJM market rates of about $75 per MW per hour for 4,000 hours per year[161]. Remaining useful life (RUL) prediction and scheduling of maintenance tasks can be achieved by state-of-health (SOH) monitoring with machine-learning approaches trained on cycling data, which helps to minimize the likelihood of unexpected capacity degradation[162].

## 9.7 Hydrogen and Fuel Cell Challenges

Hydrogen fuel cells have the theoretical potential to deliver long-duration back-up power (48+ hours proven), and produce zero direct emissions, but are still costly, inefficient and lacking in infrastructure. Microsoft's 3 MW demo project at their data center proved the technical viability, but also pointed to the cost problem: Fuel cell electricity is currently costing $150 to $250/MWh, compared to grid electricity or battery storage which cost $50 to $80/MWh at the same time[155]. The CAPEX of the electrolyzer, which ranges from $1,000-$2,000/kW, is another constraint for on-site GH production, and is decreasing as the size of the plants increases[107].

Greater fuel cell efficiency occurs at full load (55 to 60%) versus partial load (40 to 50%), resulting in an operational compromise between backup duration and efficiency[154]. Safety requirements for hydrogen storage, including pressure vessel certification, leak detection, and ventilation systems, add to the complexity and cost of fuel cell installations. The IEA expects the cost of green hydrogen to drop to $2 per kg by 2030 and $1 per kg by 2040 under the best of conditions, putting fuel cells in economic competition with data center backup by the mid-2030s[49].

## 9.8 Cooling System Integration

The coupling of cooling systems to renewable energy supply demands synchronized handling of thermal and electric energy flows. Thermal energy storage (TES) can help to defer cooling loads into hours when renewable energy is available in abundance or electricity is cheap, such as at night or during the summer. When power generation is not as high as needed, chillers freeze water into ice; when the renewable power output is less than needed, the ice is melted to provide cooling without chiller operation[86]. This thermal-electrical coupling provides opportunities for optimization but also introduces complexity into the control system, as it must control the electrical dispatch state as well as the thermal storage state simultaneously.

Another way of lowering cooling energy usage is when there are favorable conditions in the ambient environment, which is called free cooling. Free cooling can achieve 3,000 to 6,000 hours of cooling per year in temperate and cold climates, resulting in energy savings of 40 to 70 percent for chillers during this time[79]. When renewable energy is limited and cooling demands energy-intensive, a slight increase in data center inlet temperature from the traditional 20-22 degrees Celsius to 32-35 degrees Celsius can be used in dynamic setpoint management to save 15 to 25% in cooling energy usage while slightly accelerating component aging [145].

## 9.9 Cybersecurity and Operational Technology

The augmentation of the attack surface area due to integration of renewable energy systems, such as energy management platforms, smart inverters, battery management systems, and renewable monitoring systems, creates cybersecurity challenges that should be taken into account during system design. The possible threats to the system can be false data injection (providing corrupted sensor readings to the EMS), malicious control commands (causing equipment to operate outside safe parameters), and denial of service attacks (disrupting communication between components)[163]. As the IT and OT networks in the modern-day data center converge, there are opportunities for cyber threats to spread from enterprise systems to critical power infrastructure.

The following principles are followed to support best practices for OT cybersecurity: Air-gapping or VPN-protected control networks, Multi-factor authentication of all operator access, Role-based access control that minimizes the permissions of each user, Encrypted communications with TLS 1.3 or its higher versions, and Redundant communication paths to ensure control capability for disruptions to the network[164]. Relevant standards include NERC CIP (Critical Infrastructure Protection) for bulk power systems, IEC 62351 for power system communications security, and the NIST Cybersecurity Framework for overall risk management. Vulnerability scans and penetration tests should be performed at least once a year, to determine and fix security weaknesses[165].

# 10. Economic Analysis and Financial Viability

This chapter provides a comprehensive economic analysis of renewable-powered AI data centers, examining capital costs, operational expenses, levelized cost of energy, power purchase agreements, tax incentives, and financial modeling approaches. The analysis demonstrates that hybrid renewable systems are approaching or have achieved cost parity with conventional grid-powered operations in many markets.

Figures, schemes, and charts, along with their captions, should be placed in the text where they are first mentioned and numbered consecutively with Arabic numbers. In addition, the figure caption should be placed below the picture.

| (a) | (b) |
| --- | --- |

Figure 1. If there are multiple panels, please give a detailed description: (a) Description of what is contained in the first panel; (b) Description of what is contained in the second panel. A caption on a single line should be centered. Reproduced with permission.[Ref.] Copyright Year, Publisher.

((Permission statement required for all figures reproduced or adapted from previously published articles/sources. CC-BY content can be used without asking permission, but the source must be attributed: Reproduced under terms of the CC-BY license.[ref] Copyright Year, The Authors, published by [Publisher]. However, permission must be obtained for reproduction of content published under CC-BY-NC/ND/SA license; delete if not applicable.))

Table 1. Tables should be placed in the main text near to the first time they are cited.

| Title 1 | Title 2 | Title 3 |
| --- | --- | --- |
| entry 1 | data | data |
| entry 2 | data | data a |

a Tables may have a footer.

## 2.3 Formatting of Mathematical Components

The authors are encouraged to use either the Microsoft Equation Editor or the MathType add-on (http://www.mathtype.com) for equations. This is an example of an equation:

|  | (1) |
| --- | --- |

3. Conclusion

Conclusion is not merely a summary of your points or a re-statement of your research problem but a synthesis of key points, they provide clarity and insight into the topic.

Acknowledgments: Generally the last paragraph of the paper is the place to acknowledge people, organizations, and financing (you may state grant numbers and sponsors here.

Conflicts of Interest: Declare conflicts of interest or state “The authors declare no conflict of interest.” Authors must identify and declare any personal circumstances or interest that may be perceived as inappropriately influencing the representation or interpretation of reported research results. Any role of the funders in the design of the study; in the collection, analyses or interpretation of data; in the writing of the manuscript, or in the decision to publish the results must be declared in this section. If there is no role, please state “The funders had no role in the design of the study; in the collection, analyses, or interpretation of data; in the writing of the manuscript, or in the decision to publish the results”. In particular, if any author is editor or editor-in-chief of this journal, please state “XX is an editorial board member/editor-in-chief for Space Solar Power & Wireless Transmission and was not involved in the editorial review or the decision to publish this article. All authors declare that there are no competing interests.”

Supplementary Materials/ Appendix A

The appendix is an optional section that can contain details and data supplemental to the main text. All appendix sections must be cited in the main text.

References

[1]	IEA, “Data Centres and Data Transmission Networks.” [Online]. Available: https://www.iea.org/energy-system/buildings/data-centres-and-data-transmission-networks

[2]	A. Shehabi et al., “United States Data Center Energy Usage Report,” LBNL--1005775, 1372902, Jun. 2016. doi: 10.2172/1372902.

[3]	IEA, “Energy and AI.” Accessed: Apr. 10, 2025. [Online]. Available: https://www.iea.org/reports/energy-and-ai

[4]	D. Patterson et al., “Carbon Emissions and Large Neural Network Training,” 2021, arXiv. doi: 10.48550/ARXIV.2104.10350.

[5]	E. Strubell, A. Ganesh, and A. McCallum, “Energy and Policy Considerations for Deep Learning in NLP,” 2019, arXiv. doi: 10.48550/ARXIV.1906.02243.

[6]	F. Jeanquartier et al., “Assessing the carbon footprint of language models: Towards sustainability in AI,” Resour. Conserv. Recycl., vol. 226, p. 108670, Feb. 2026, doi: 10.1016/j.resconrec.2025.108670.

[7]	J. Shi, Z. Yang, and D. Lo, “Efficient and Green Large Language Models for Software Engineering: Literature Review, Vision, and the Road Ahead,” Dec. 04, 2024, arXiv: arXiv:2404.04566. doi: 10.48550/arXiv.2404.04566.

[8]	X. Chen, X. Wang, A. Colacelli, M. Lee, and L. Xie, “Electricity Demand and Grid Impacts of AI Data Centers: Challenges and Prospects,” Nov. 26, 2025, arXiv: arXiv:2509.07218. doi: 10.48550/arXiv.2509.07218.

[9]	D. Donnellan et al., “Uptime Institute Global Data Center Survey 2024,” 2024.

[10]	M. Andersch et al., “NVIDIA Hopper Architecture In-Depth”.

[11]	K. Calvin et al., “IPCC, 2023: Climate Change 2023: Synthesis Report. Contribution of Working Groups I, II and III to the Sixth Assessment Report of the Intergovernmental Panel on Climate Change [Core Writing Team, H. Lee and J. Romero (eds.)]. IPCC, Geneva, Switzerland.,” Intergovernmental Panel on Climate Change (IPCC), Jul. 2023. doi: 10.59327/IPCC/AR6-9789291691647.

[12]	“Driving sustainable innovation for society.” [Online]. Available: https://datacenters.google/operating-sustainably/

[13]	D. Feldman et al., “Spring 2024 Solar Industry Update,” NREL/PR--7A40-90042, 2376145, MainId:91820, May 2024. doi: 10.2172/2376145.

[14]	“Renewable power generation costs in 2023”.

[15]	IEA, “Wind.” Accessed: Feb. 25, 2025. [Online]. Available: https://www.iea.org/energy-system/renewables/wind

[16]	“Renewable power generation costs in 2024”, [Online]. Available: https://www.rinnovabili.it/wp-content/uploads/2025/07/IRENA-RENEWABLE-POWER-GENERATION-COSTS-IN-2024.pdf

[17]	BNEF, “BNEF: Lithium-ion battery pack prices fall to $108/kWh, stationary storage becomes lowest price segment.” Accessed: Dec. 09, 2025. [Online]. Available: https://www.ess-news.com/2025/12/09/bnef-lithium-ion-battery-pack-prices-fall-to-108-kwh-stationary-storage-becomes-lowest-price-segment/

[18]	G. Song, B. Cao, and L. Chang, “Review of Grid-forming Inverters in Support of Power System Operation,” Chin. J. Electr. Eng., vol. 8, no. 1, pp. 1–15, Mar. 2022, doi: 10.23919/CJEE.2022.000001.

[19]	G. Rostirolla et al., “A survey of challenges and solutions for the integration of renewable energy in datacenters,” Renew. Sustain. Energy Rev., vol. 155, p. 111787, Mar. 2022, doi: 10.1016/j.rser.2021.111787.

[20]	D. Harrison-Atlas, C. Murphy, A. Schleifer, and N. Grue, “Temporal complementarity and value of wind-PV hybrid systems across the United States,” Renew. Energy, vol. 201, pp. 111–123, Dec. 2022, doi: 10.1016/j.renene.2022.10.060.

[21]	C. Wu, X.-P. Zhang, and M. Sterling, “Solar power generation intermittency and aggregation,” Sci. Rep., vol. 12, no. 1, p. 1363, Jan. 2022, doi: 10.1038/s41598-022-05247-2.

[22]	IEEE Standard for Harmonic Control in Electric Power Systems. doi: 10.1109/IEEESTD.2022.9848440.

[23]	M. C. Offutt and L. Zhu, “Data Centers and Their Energy Consumption: Frequently Asked Questions”.

[24]	“Improvements to Generator Interconnection Procedures and Agreements.” Accessed: Sep. 06, 2023. [Online]. Available: https://www.federalregister.gov/documents/2023/09/06/2023-16628/improvements-to-generator-interconnection-procedures-and-agreements

[25]	S. Cai and Z. Gou, “Towards energy-efficient data centers: A comprehensive review of passive and active cooling strategies,” Energy Built Environ., vol. 7, no. 1, pp. 206–226, Feb. 2026, doi: 10.1016/j.enbenv.2024.08.009.

[26]	R. Mural et al., “AI, Data Centers, and the U.S. Electric Grid: A Watershed Moment”.

[27]	C. Zhao, W. Gao, F. Nie, and H. Zhou, “A Survey of GPU Multitasking Methods Supported by Hardware Architecture,” IEEE Trans. Parallel Distrib. Syst., vol. 33, no. 6, pp. 1451–1463, Jun. 2022, doi: 10.1109/TPDS.2021.3115630.

[28]	V. Avelar and P. Donovan, “How 6 AI Attributes Change Data Center Design”.

[29]	T. B. Brown et al., “Language Models are Few-Shot Learners,” 2020, arXiv. doi: 10.48550/ARXIV.2005.14165.

[30]	M. Raza, “Carbon Literacy for Generative AI: Visualizing Training Emissions Through Human-Scale Equivalents”.

[31]	Google, “Growing the internet while reducing energy consumption.” [Online]. Available: Growing the internet while reducing energy consumption

[32]	D. Al Kez, A. M. Foley, F. W. B. M. Hasan Wong, A. Dolfi, and G. Srinivasan, “AI-driven cooling technologies for high-performance data centres: state-of-the-art review and future directions,” Sustain. Energy Technol. Assess., vol. 82, p. 104511, Oct. 2025, doi: 10.1016/j.seta.2025.104511.

[33]	X. Zhang, T. Lindberg, N. Xiong, V. Vyatkin, and A. Mousavi, “Cooling Energy Consumption Investigation of Data Center IT Room with Vertical Placed Server,” Energy Procedia, vol. 105, pp. 2047–2052, May 2017, doi: 10.1016/j.egypro.2017.03.581.

[34]	M. Azarifar, M. Arik, and J.-Y. Chang, “Liquid cooling of data centers: A necessity facing challenges,” Appl. Therm. Eng., vol. 247, p. 123112, Jun. 2024, doi: 10.1016/j.applthermaleng.2024.123112.

[35]	D. Zhou et al., “Accelerating liquid cooling adoption in data centers: necessity, challenges and solutions,” Technol. Rev. Carbon Neutrality, p. 9550014, Dec. 2025, doi: 10.26599/TRCN.2025.9550014.

[36]	J. Hurni et al., “Over 31%-efficient perovskite–TOPCon solar cells enabled by AlO x  -based hydrogenation and front sub-micron texturing,” EES Sol., vol. 1, no. 5, pp. 732–735, 2025, doi: 10.1039/D5EL00105F.

[37]	G. Galioto, G. Vitale, A. Sferlazza, G. Lullo, and G. C. Giaconia, “Wide and Ultrawide Bandgap Power Semiconductors: A Comprehensive System-Level Review,” Electronics, vol. 15, no. 4, p. 835, Feb. 2026, doi: 10.3390/electronics15040835.

[38]	P. Blecich, I. Bonefačić, T. Senčić, and I. Wolf, “Resilience Under Heatwaves: Croatia’s Power System During the July 2024 Heatwave and the Role of Variable Renewable Energy by 2030,” Appl. Sci., vol. 15, no. 12, p. 6440, Jun. 2025, doi: 10.3390/app15126440.

[39]	G. Gülen, J. Das, and M. H. Young, “Assessing Economic Costs of Two Reliable Generation Mix Scenarios in the ERCOT System,” Energies, vol. 19, no. 9, p. 2195, May 2026, doi: 10.3390/en19092195.

[40]	A. McCoy et al., “Offshore Wind Market Report: 2024 Edition”.

[41]	N. Lukač, G. Štumberger, and B. Žalik, “Wind resource assessment using airborne LiDAR data and smoothed particle hydrodynamics,” Environ. Model. Softw., vol. 95, pp. 1–12, Sep. 2017, doi: 10.1016/j.envsoft.2017.05.006.

[42]	E. Virguez et al., “Renewable energy quality trilemma and coincident wind and solar droughts”, doi: 10.17615/C4JD-4Y42.

[43]	M. Bošnjaković, N. Veljić, J. T. Božič, and S. Muhič, “SWOT-AHP Analysis of the Importance and Adoption of Pumped-Storage Hydropower,” Technologies, vol. 13, no. 7, p. 305, Jul. 2025, doi: 10.3390/technologies13070305.

[44]	M. Catania, F. Parolin, F. Fattori, and P. Colbertaldo, “The role of hydropower in decarbonisation scenarios,” Renew. Energy, vol. 236, p. 121411, Dec. 2024, doi: 10.1016/j.renene.2024.121411.

[45]	S. Evro, A. Ajumobi, D. Mayon, and O. S. Tomomewo, “Navigating battery choices: A comparative study of lithium iron phosphate and nickel manganese cobalt battery technologies,” Future Batter., vol. 4, p. 100007, Dec. 2024, doi: 10.1016/j.fub.2024.100007.

[46]	K. Chandra Bhowmik, Md. A. Rahman, Md. M. Billah, and A. Paul, “From Lithium‐Ion to Sodium‐Ion Batteries for Sustainable Energy Storage: A Comprehensive Review on Recent Research Advancements and Perspectives,” Chem. Rec., vol. 24, no. 12, p. e202400176, Dec. 2024, doi: 10.1002/tcr.202400176.

[47]	A. Barzigar, E. Ebadati, A. S. Mujumdar, and S. M. Hosseinalipour, “A comprehensive review of vanadium redox flow batteries: Principles, benefits, and applications,” Res., vol. 2, no. 4, p. 100767, Dec. 2025, doi: 10.1016/j.nexres.2025.100767.

[48]	European Commission. Joint Research Centre et al., Clean Energy Technology Observatory. in EUR. LU: Publications Office of the European Union, 2026. doi: 10.2760/2686206.

[49]	U. Remme, “Global Hydrogen Review 2025,” 2025, [Online]. Available: https://iea.blob.core.windows.net/assets/12d92ecc-e960-40f3-aff5-b2de6690ab6b/GlobalHydrogenReview2025.pdf

[50]	T. Jaradat and T. Khatib, “A review of battery energy storage system for renewable energy penetration in electrical power system: Environmental impact, sizing methods, market features, and policy frameworks,” Future Batter., vol. 7, p. 100106, Sep. 2025, doi: 10.1016/j.fub.2025.100106.

[51]	M. M. Rana, H. Mo, G. M. Shafiullah, L. Qiao, and D. Dong, “Optimal sizing of battery storage for cost-effective peak shaving in regional distribution networks,” J. Energy Storage, vol. 141, p. 119502, Jan. 2026, doi: 10.1016/j.est.2025.119502.

[52]	Z. Ma, “From Grid-Following to Grid-Forming: A Review of Converter Technology Paradigm Shift and Its Applications in Renewable-Rich Power Systems,” Adv. Eng. Res. Possibilities Chall., vol. 2, no. 2, p. 37, Aug. 2025, doi: 10.63313/AERpc.9047.

[53]	IEEE Standard for Interconnection and Interoperability of Inverter-Based Resources (IBRs) Interconnecting with Associated Transmission Electric Power Systems. doi: 10.1109/IEEESTD.2022.9762253.

[54]	S. Shelar, D. Bankar, and S. Bakre, “Review of revisions of IEEE 519 Standard on Power System Harmonics (1981 to 2022),” in 2024 21st International Conference on Harmonics and Quality of Power (ICHQP), Chengdu, China: IEEE, Oct. 2024, pp. 415–420. doi: 10.1109/ICHQP61174.2024.10768696.

[55]	Google, “Google Environmental Report 2025.” [Online]. Available: https://sustainability.google/reports/google-2025-environmental-report/

[56]	O. A. Mavisclara et al., “The AI-Driven Energy Surge: A comprehensive review of sustainable power solutions for data centers,” Glob. J. Eng. Technol. Adv., vol. 24, no. 3, pp. 328–344, Sep. 2025, doi: 10.30574/gjeta.2025.24.3.0279.

[57]	Meta, “2025 Sustainability Report.” [Online]. Available: https://sustainability.atmeta.com/wp-content/uploads/2025/08/Meta_2025-Sustainability-Report.pdf

[58]	BloombergNEF, “Corporate Clean Energy Buying Fell in 2025 After Nearly a Decade of Growth.”

[59]	Y. Panchal, S. Dubey, and R. Pathak, “Exploring the Future of Cloud Computing: A Comprehensive Study of Microsoft’s Underwater Data Centers,” vol. 12, no. 3, 2025.

[60]	K. Simon, “Project Natick — Microsoft’s Self-sufficient Underwater Datacenters”.

[61]	G. Gülen, J. Das, and M. H. Young, “Assessing Economic Costs of Two Reliable Generation Mix Scenarios in the ERCOT System,” Energies, vol. 19, no. 9, p. 2195, May 2026, doi: 10.3390/en19092195.

[62]	Equinix, “Sustainability Report 2025.” [Online]. Available: https://delivery-p112322-e1154416.adobeaemcloud.com/adobe/assets/deliver/urn:aaid:aem:116e6fc1-6217-4132-8fcf-1dc7096396df/Equinix-Inc_2025_Sustainability-Report.pdf

[63]	B. L. Willis et al., “Sustainability outlook for leading silicon photovoltaic technologies from 2023–2034 in Europe,” EPJ Photovolt., vol. 17, p. 16, 2026, doi: 10.1051/epjpv/2026009.

[64]	Apple, “Environmental Progress Report.” [Online]. Available: https://www.apple.com/environment/pdf/Apple_Environmental_Progress_Report_2025.pdf

[65]	IEEE Recommended Practice for the Design of Reliable Industrial and Commercial Power Systems (Gold Book). doi: 10.1109/IEEESTD.1998.89291.

[66]	I. Keskin and G. Soykan, “Reliability, availability, and life-cycle cost (LCC) analysis of combined cooling, heating and power (CCHP) integration to data centers considering electricity and cooling supplies,” Energy Convers. Manag., vol. 291, p. 117254, Sep. 2023, doi: 10.1016/j.enconman.2023.117254.

[67]	Nguyen Anh Huy and X. T. Nguyen, “Data center energy assessment process and energy efficiency metrics,” 2025, doi: 10.13140/RG.2.2.27710.75845.

[68]	J. Gavrila Mailuhu, M. A.F. Haurissa, and M. Jamlaay, “Design And Construction Of Automatic Transfer Switch (ATS) System With Backup Control System In Hybrid Power Plant (PLN - PLTS - GENSET),” Int. J. Sci. Technol. Manag., vol. 6, no. 3, pp. 520–527, Jun. 2025, doi: 10.46729/ijstm.v6i3.1316.

[69]	S. Narayanaswamy, P. D. Patel, I. Karlin, A. Gupta, S. Saripalli, and J. Guo, “Datacenter Energy Optimized Power Profiles,” 2025, arXiv. doi: 10.48550/ARXIV.2510.03872.

[70]	V. Singhania, S. Aga, and M. A. Ibrahim, “FinGraV: Methodology for Fine-Grain GPU Power Visibility and Insights,” Mar. 28, 2025, arXiv: arXiv:2412.12426. doi: 10.48550/arXiv.2412.12426.

[71]	Z. Yang, G. He, Y. Li, Y. Sun, W. Luo, and W. Zhang, “Thermal management in copackaged optics: from device assembly to system operation,” Adv. Photonics Nexus, vol. 5, no. 03, Mar. 2026, doi: 10.1117/1.APN.5.3.034001.

[72]	S. Mohammadi et al., “Grid Integration of AI Data Centers: A Critical Review of Energy Storage Solutions,” May 05, 2026, arXiv: arXiv:2603.00415. doi: 10.48550/arXiv.2603.00415.

[73]	Niranchana Radhakrishnan, “Optimizing Data Centre Energy Efficiency with Dynamic Resource Allocation and Intelligent Cooling Management through Machine Learning,” J. Electr. Syst., vol. 20, no. 3s, pp. 286–293, Apr. 2024, doi: 10.52783/jes.1287.

[74]	T. W. A. Putra, N. D. Setiawan, and R. Rusito, “The Use of Machine Learning for Efficient Energy Management in Big Data-Based Computing Systems,” J. Technol. Inform. Eng., vol. 3, no. 3, pp. 324–336, Dec. 2024, doi: 10.51903/jtie.v3i3.202.

[75]	IEC, “Electrical Energy Storage.” [Online]. Available: https://iec.ch/system/files/2019-09/content/media/files/iec_wp-electrical_energy_storage-en.pdf

[76]	Y. Sheng et al., “Power for AI Data Centers: Energy Demand, Grid Impacts, Challenges and Perspectives,” Energies, vol. 19, no. 3, p. 722, Jan. 2026, doi: 10.3390/en19030722.

[77]	E. Eslami, “Air Quality and Greenhouse Gas Emissions Assessment of Data Centers in Texas: Quantifying Impacts and Environmental Tradeoffs,” 2025, arXiv. doi: 10.48550/ARXIV.2509.21312.

[78]	Y. Tang, X. Bai, C. Jin, Y. Fu, W. Mao, and X. Xu, “Experimental and numerical study on the thermal environment of a data center,” Build. Environ., vol. 212, p. 108741, Mar. 2022, doi: 10.1016/j.buildenv.2021.108741.

[79]	C. S. D. and S. Abimannan, “Energy Efficient Free Cooling System for Data Centers,” in 2011 IEEE Third International Conference on Cloud Computing Technology and Science, Athens, Greece: IEEE, Nov. 2011, pp. 646–651. doi: 10.1109/CloudCom.2011.100.

[80]	J. Yuan, Y. Yan, X. Zhang, X. Kong, and T. Zhang, “Coupling of flexible phase change materials and servers for improving the security of data centers in emergency situations,” Appl. Therm. Eng., vol. 242, p. 122439, Apr. 2024, doi: 10.1016/j.applthermaleng.2024.122439.

[81]	IEEE Recommended Practice for Powering and Grounding Electronic Equipment. doi: 10.1109/IEEESTD.1999.90559.

[82]	R. Siddique, “Active Power Filters for Harmonic Mitigation in Power Systems”.

[83]	A. Santos, G. Duggan, S. Frank, D. Gerber, and D. Zimmerle, “Endpoint Use Efficiency Comparison for AC and DC Power Distribution in Commercial Buildings,” Energies, vol. 14, no. 18, p. 5863, Sep. 2021, doi: 10.3390/en14185863.

[84]	A. F. Snyder and M. T. G. Stuber, “The ANSI C12 protocol suite - updated and now with network capabilities,” in 2007 Power Systems Conference: Advanced Metering, Protection, Control, Communication, and Distributed Resources, Clemson, SC, USA: IEEE, Mar. 2007, pp. 117–122. doi: 10.1109/PSAMP.2007.4740906.

[85]	J. Li, C. Wang, and Y. Liu, “AI Driven Virtual Power Plants: A Comprehensive Review,” Jan. 22, 2026, Engineering. doi: 10.20944/preprints202601.1691.v1.

[86]	S. Jadhav and Z. Liu, “Digital Twin-Based Cooling System Optimization for Data Center,” 2026, arXiv. doi: 10.48550/ARXIV.2603.01198.

[87]	NREL, “National Renewable Energy Laboratory (NREL). (2026).” [Online]. Available: https://atb.nrel.gov/

[88]	NREL, “National Renewable Energy Laboratory (NREL).” [Online]. Available: https://www.google.com/search?q=https://atb.nrel.gov/electricity

[89]	E. Förstner et al., “Photovoltaic system reduces grid voltage waveform distortions in the frequency range from 700 Hz to 1250 Hz,” 2026, doi: 10.5445/IR/1000191363.

[90]	L. Liu, H. Matayoshi, M. E. Lotfy, M. Datta, and T. Senjyu, “Load Frequency Control Using Demand Response and Storage Battery by Considering Renewable Energy Sources,” Energies, vol. 11, no. 12, p. 3412, Dec. 2018, doi: 10.3390/en11123412.

[91]	O. Ndindayino, A. Puel, and J. Meyers, “Effect of blockage on wind turbine power and wake development,” Feb. 12, 2025, Fluid mechanics/Wakes and wind farm aerodynamics. doi: 10.5194/wes-2025-6.

[92]	P. Toufani, E. C. Karakoyun, E. Nadar, O. B. Fosso, and A. S. Kocaman, “Optimization of pumped hydro energy storage systems under uncertainty: A review,” J. Energy Storage, vol. 73, p. 109306, Dec. 2023, doi: 10.1016/j.est.2023.109306.

[93]	J. F. S. De Paula, J. L. De Souza Silva, M. V. De Paula, G. Fraidenraich, and T. A. Dos Santos Barros, “A Two-Stage Methodology for Accurate PV Energy Yield Estimation Using Satellite Weather Data and PV Modeling Python Library,” in 2025 Brazilian Power Electronics Conference (COBEP), Vitoria, Brazil: IEEE, Oct. 2025, pp. 1–6. doi: 10.1109/COBEP66423.2025.11231587.

[94]	M. Ernst and J. Gooday, “Methodology for generating high time resolution typical meteorological year data for accurate photovoltaic energy yield modelling,” Sol. Energy, vol. 189, pp. 299–306, Sep. 2019, doi: 10.1016/j.solener.2019.07.069.

[95]	A. K. Nassar et al., “Multi-criteria GIS-based approach for optimal site selection of solar and wind energy,” Unconv. Resour., vol. 7, p. 100192, Jul. 2025, doi: 10.1016/j.uncres.2025.100192.

[96]	T. Anderson, “An improved typical meteorological year for solar energy simulations in Rarotonga, Cook Islands,” J. R. Soc. N. Z., vol. 52, no. 5, pp. 606–613, Oct. 2022, doi: 10.1080/03036758.2021.2013262.

[97]	C. Jung and D. Schindler, “Projections of energy yield- and complementarity-driven wind energy expansion scenarios in the European Union,” Energy Convers. Manag., vol. 269, p. 116160, Oct. 2022, doi: 10.1016/j.enconman.2022.116160.

[98]	M. Li et al., “Renewable energy quality trilemma and coincident wind and solar droughts,” Commun. Earth Environ., vol. 5, no. 1, p. 661, Nov. 2024, doi: 10.1038/s43247-024-01850-5.

[99]	S. Jerez, I. Tobin, M. Turco, P. Jiménez-Guerrero, R. Vautard, and J. P. Montávez, “Future changes, or lack thereof, in the temporal variability of the combined wind-plus-solar power production in Europe,” Renew. Energy, vol. 139, pp. 251–260, Aug. 2019, doi: 10.1016/j.renene.2019.02.060.

[100]	X.-R. Zhu, J.-H. Tian, and Y. Wang, “The impact of climate change on wind and solar photovoltaic power potential and distribution in China,” Adv. Clim. Change Res., vol. 16, no. 4, pp. 730–746, Aug. 2025, doi: 10.1016/j.accre.2025.04.015.

[101]	W. Cole, V. Ramasamy, and M. Turan, “Cost Projections for Utility-Scale Battery Storage: 2025 Update,” Renew. Energy, 2025, [Online]. Available: https://docs.nrel.gov/docs/fy25osti/93281.pdf

[102]	Our World in Data, “Battery costs have declined by 99% in the last three decades, making electrified transport a reality.” [Online]. Available: https://ourworldindata.org/battery-price-decline

[103]	Y. Xie et al., “A high-fidelity online monitoring algorithm for multiple physical fields in battery pack,” Appl. Energy, vol. 398, p. 126443, Nov. 2025, doi: 10.1016/j.apenergy.2025.126443.

[104]	J. Vaičys, S. Gudžius, A. Jonaitis, R. Račkienė, A. Blinov, and D. Peftitsis, “A case study of optimising energy storage dispatch: Convex optimisation approach with degradation considerations,” J. Energy Storage, vol. 97, p. 112941, Sep. 2024, doi: 10.1016/j.est.2024.112941.

[105]	D. Reber, S. Jarvis, and M. Marshak, “The role of energy density for grid-scale batteries,” Nov. 17, 2022. doi: 10.26434/chemrxiv-2022-5ddhs.

[106]	S. Rahman and T. A. Khan, “Energy Storage Systems for AI Data Centers: A Review of Technologies, Characteristics, and Applicability,” Energies, vol. 19, no. 3, p. 634, Jan. 2026, doi: 10.3390/en19030634.

[107]	F. Yang, Z. Wang, and X. Tian, “Estimating future costs of hydrogen as long-duration energy storage based on a learning rate approach,” Clean Energy, vol. 10, no. 2, pp. 146–155, Mar. 2026, doi: 10.1093/ce/zkaf075.

[108]	X. Dong, Z. Yang, Q. Zhu, J. Li, B. Zhou, and J. Zhu, “Research on Reliability Evaluation Method of Distribution Network Considering the Temporal Characteristics of Distributed Power Sources,” Processes, vol. 14, no. 8, p. 1296, Apr. 2026, doi: 10.3390/pr14081296.

[109]	S. Babamohammadi, A. R. Birss, H. Pouran, J. Pandhal, and T. N. Borhani, “Emission control and carbon capture from diesel generators and engines: A decade-long perspective,” Carbon Capture Sci. Technol., vol. 14, p. 100379, Mar. 2025, doi: 10.1016/j.ccst.2025.100379.

[110]	S. Ghosh and J. Damodara, “Scalable data centers – Power generation and delivery challenges and solutions,” Energy Rep., vol. 15, p. 109178, Jun. 2026, doi: 10.1016/j.egyr.2026.109178.

[111]	Idaho National Lab, “Powering Data Centers with Clean Energy.” [Online]. Available: https://gain.inl.gov/content/uploads/4/2024/11/INL-RPT-24-79307-Powering-Data-Cneters-with-Clean-Energy.pdf

[112]	EPRI, “Powering Data Centers in the AI Era.” [Online]. Available: https://energie.hec.ca/wp-content/uploads/2025/10/PPT_EPRI.pdf

[113]	EIA, “Electric Power Annual 2024.” [Online]. Available: https://www.eia.gov/electricity/annual/pdf/epa.pdf

[114]	J. W. Zhang, Y. H. Wang, G. C. Liu, and G. Z. Tian, “A review of control strategies for flywheel energy storage system and a case study with matrix converter,” Energy Rep., vol. 8, pp. 3948–3963, Nov. 2022, doi: 10.1016/j.egyr.2022.03.009.

[115]	Y. A. Sultan, S. S. Kaddah, and M. A. Elhosseini, “Enhancing smart grid transient performance using storage device‐based MPC controller,” IET Renew. Power Gener., vol. 11, no. 10, pp. 1316–1324, Aug. 2017, doi: 10.1049/iet-rpg.2016.0892.

[116]	Y. Hu, Z. Li, and J. Cui, “An economic model predictive control strategy for EV-integrated microgrids considering battery degradation,” Energy, vol. 335, p. 138205, Oct. 2025, doi: 10.1016/j.energy.2025.138205.

[117]	L. Bongini, R. A. Mastromauro, D. Sgrò, and F. Malvaldi, “Electrical Damping Assessment and Stability Considerations for a Highly Electrified Liquefied Natural Gas Plant,” Energies, vol. 13, no. 10, p. 2612, May 2020, doi: 10.3390/en13102612.

[118]	R. D. Zimmerman, C. E. Murillo-Sanchez, and R. J. Thomas, “MATPOWER: Steady-State Operations, Planning, and Analysis Tools for Power Systems Research and Education,” IEEE Trans. Power Syst., vol. 26, no. 1, pp. 12–19, Feb. 2011, doi: 10.1109/TPWRS.2010.2051168.

[119]	A. J. Monticelli, A. Garcia, and O. R. Saavedra, “Fast decoupled load flow: hypothesis, derivations, and testing,” IEEE Trans. Power Syst., vol. 5, no. 4, pp. 1425–1431, Nov. 1990, doi: 10.1109/59.99396.

[120]	M. Huneault and F. D. Galiana, “A survey of the optimal power flow literature,” IEEE Trans. Power Syst., vol. 6, no. 2, pp. 762–770, May 1991, doi: 10.1109/59.76723.

[121]	Xiaokang Xu, M. F. Kandlawala, and Ming Wu, “NERC TPL-001-4 transient voltage performance compliance study - criteria development, study methodology and case studies,” in 2016 IEEE Power and Energy Society General Meeting (PESGM), Boston, MA, USA: IEEE, Jul. 2016, pp. 1–5. doi: 10.1109/PESGM.2016.7741072.

[122]	A. Fernandez-Guillamon, A. Molina-Garcia, K. Das, and M. Altin, “Comparison of different tools for power flow analysis with high wind power integration,” in 2019 International Conference on Clean Electrical Power (ICCEP), Otranto, Italy: IEEE, Jul. 2019, pp. 82–86. doi: 10.1109/ICCEP.2019.8890163.

[123]	V. Geekiyanage and J. Seppänen, “Power System Stability Improvements Through Grid Forming Inverters for Systems with High Penetration of Grid Following Inverters,” in 2024 IEEE PES Innovative Smart Grid Technologies Europe (ISGT EUROPE), Dubrovnik, Croatia: IEEE, Oct. 2024, pp. 1–5. doi: 10.1109/ISGTEUROPE62998.2024.10863434.

[124]	IEEE Standard for the Specification of Microgrid Controllers. doi: 10.1109/IEEESTD.2018.8340204.

[125]	J. S. Ali, Y. Qiblawey, A. Alassi, A. M. Massoud, S. M. Muyeen, and H. Abu-Rub, “Power System Stability With High Penetration of Renewable Energy Sources: Challenges, Assessment, and Mitigation Strategies,” IEEE Access, vol. 13, pp. 39912–39934, 2025, doi: 10.1109/ACCESS.2025.3546491.

[126]	NERC, “Inverter-Based Resource Performance Issues.” [Online]. Available: https://www.nerc.com/globalassets/programs/bpsa/alerts/2023/nerc-alert-r-2023-03-14-01-level-2---inverter-based-resource-performance-issues.pdf

[127]	J. C. Das, Power System Harmonics and Passive Filter Designs, 1st ed. Wiley, 2015. doi: 10.1002/9781118887059.

[128]	M. S. Anindya, F. Zaro, and M. Popescu, “Power Quality Improvement Using Active Power Filters in Industrial Systems,” RESWARA J. Ris. Ilmu Tek., vol. 3, no. 2, pp. 44–50, Apr. 2025, doi: 10.70716/reswara.v3i2.404.

[129]	HOMER, “Microgrid and Hybrid Power Modeling.” [Online]. Available: https://homerenergy.com/

[130]	“MODELING, SIMULATION AND INTELLIGENT ALGORITHMS FOR SOLVING THE MACHINE-LOADING PROBLEM: A LITERATURE REVIEW,” in Proceedings of THE 22ND INTERNATIONAL CONFERENCE ON MODELING AND APPLIED SIMULATION, CAL-TEK srl, 2023. doi: 10.46354/i3m.2023.mas.013.

[131]	R. Rogersten, L. Vanfretti, and W. Li, “Towards consistent model exchange and simulation of VSC-HVdc controls for EMT studies,” in 2015 IEEE Power & Energy Society General Meeting, Denver, CO, USA: IEEE, Jul. 2015, pp. 1–5. doi: 10.1109/PESGM.2015.7285986.

[132]	A. N. Rosli, S. H. Yusoff, H. Mansor, S. N. M. Sapihie, and M. A. M. M. Fahmi, “Using Model Predictive Control in Renewable Energy Sources,” in 2023 IEEE 9th International Conference on Smart Instrumentation, Measurement and Applications (ICSIMA), Kuala Lumpur, Malaysia: IEEE, Oct. 2023, pp. 263–268. doi: 10.1109/ICSIMA59853.2023.10373520.

[133]	J. M. Morales, A. J. Conejo, H. Madsen, P. Pinson, and M. Zugno, Integrating Renewables in Electricity Markets: Operational Problems, 1st ed. 2014. in International Series in Operations Research & Management Science, no. 205. New York, NY: Springer US : Imprint: Springer, 2014. doi: 10.1007/978-1-4614-9411-9.

[134]	R. H. Inman, H. T. C. Pedro, and C. F. M. Coimbra, “Solar forecasting methods for renewable energy integration,” Prog. Energy Combust. Sci., vol. 39, no. 6, pp. 535–576, Dec. 2013, doi: 10.1016/j.pecs.2013.06.002.

[135]	U. Cali et al., “Generative AI and LLM applications in renewable energy and smart grids: a systematic review for the sustainable energy transition,” Artif. Intell. Rev., Apr. 2026, doi: 10.1007/s10462-026-11545-2.

[136]	E. Hosseini et al., “Reinforcement learning-based energy management system for lithium-ion battery storage in multilevel microgrid,” J. Energy Storage, vol. 109, p. 115114, Feb. 2025, doi: 10.1016/j.est.2024.115114.

[137]	N. Subramanian and A. A. Stonier, “Digital twin applications and case studies in modern power grid management,” Energy Rep., vol. 15, p. 109218, Jun. 2026, doi: 10.1016/j.egyr.2026.109218.

[138]	H. Chen, X. Feng, Q. Chen, and R. Han, “The Application of Machine Learning in Power Grid,” in 2024 Boao New Power System International Forum - Power System and New Energy Technology Innovation Forum (NPSIF), Qionghai, China: IEEE, Dec. 2024, pp. 568–576. doi: 10.1109/NPSIF64134.2024.10883453.

[139]	R. Schaeffer et al., “Energy sector vulnerability to climate change: A review,” Energy, vol. 38, no. 1, pp. 1–12, Feb. 2012, doi: 10.1016/j.energy.2011.11.056.

[140]	M. A. Bekhti, L. Ghomri, H. L. Beklaouz, and R. Bouddou, “Techno-economic and environmental optimization of standalone hybrid energy systems using advanced energy storage for remote electrification in Southern Algeria,” J. Renew. Sustain. Energy, vol. 17, no. 5, p. 056309, Sep. 2025, doi: 10.1063/5.0297401.

[141]	M. T. Takci, M. Qadrdan, J. Summers, and J. Gustafsson, “Data centres as a source of flexibility for power systems,” Energy Rep., vol. 13, pp. 3661–3671, Jun. 2025, doi: 10.1016/j.egyr.2025.03.020.

[142]	X. Li, Z. Zhao, X. Jiang, Y. Chen, and R. He, “A Review on AI-Driven Optimization of Data Center Energy Efficiency and Thermal Management,” Int. J. Appl. Sci., vol. 8, no. 3, p. p108, Sep. 2025, doi: 10.30560/ijas.v8n3p108.

[143]	A. Radovanovic et al., “Carbon-Aware Computing for Datacenters,” 2021, arXiv. doi: 10.48550/ARXIV.2106.11750.

[144]	T. Sukprasert, A. Souza, N. Bashir, D. Irwin, and P. Shenoy, “On the Limitations of Carbon-Aware Temporal and Spatial Workload Shifting in the Cloud,” in Proceedings of the Nineteenth European Conference on Computer Systems, Athens Greece: ACM, Apr. 2024, pp. 924–941. doi: 10.1145/3627703.3650079.

[145]	M. D. E. Gouaouri, M. Bagaa, S. Ouahouah, M. A. Ouameur, and A. Ksentini, “Enabling Power-Awareness for Kubernetes Scheduling Through Multi-Criteria Optimization,” in ICC 2025 - IEEE International Conference on Communications, Montreal, QC, Canada: IEEE, Jun. 2025, pp. 1500–1505. doi: 10.1109/ICC52391.2025.11160865.

[146]	S. Sarkar et al., “Carbon Footprint Reduction for Sustainable Data Centers in Real-Time,” 2024, arXiv. doi: 10.48550/ARXIV.2403.14092.

[147]	J. Sefyrin, “Sustainable datacentres and eco-modernist frictions in Sweden,” Inf. Commun. Soc., pp. 1–17, Dec. 2025, doi: 10.1080/1369118X.2025.2596872.

[148]	Lazard, “Levelized Cost of Energy.” [Online]. Available: https://www.lazard.com/media/eijnqja3/lazards-lcoeplus-june-2025.pdf

[149]	EPA, “Summary of Inflation Reduction Act provisions related to renewable energy.” [Online]. Available: https://www.epa.gov/green-power-markets/summary-inflation-reduction-act-provisions-related-renewable-energy

[150]	J. Rand et al., “Characteristics of Power Plants Seeking Transmission Interconnection As of the End of 2024”.

[151]	M. S. Hoosain, B. S. Paul, S. Kass, and S. Ramakrishna, “Tools Towards the Sustainability and Circularity of Data Centers,” Circ. Econ. Sustain., vol. 3, no. 1, pp. 173–197, Mar. 2023, doi: 10.1007/s43615-022-00191-9.

[152]	NFPA, “NFPA 110 Type 10 Requirements for Emergency Power Systems.” [Online]. Available: https://www.cummins.com/sites/default/files/2019-03/PowerHour_NFPA110.pdf

[153]	R. Kasperzak, M. Kureljusic, L. Reisch, and S. Thies, “Accounting for Carbon Emissions—Current State of Sustainability Reporting Practice under the GHG Protocol,” Sustainability, vol. 15, no. 2, p. 994, Jan. 2023, doi: 10.3390/su15020994.

[154]	J. Kim et al., “Reviewing the socio-technical dynamics of AI, data centers and digitalization on energy and the environment,” Renew. Sustain. Energy Rev., vol. 234, p. 116861, Jul. 2026, doi: 10.1016/j.rser.2026.116861.

[155]	G. Soyturk and O. Kizilkan, “Modeling and analysis of solid oxide fuel cell-based multigeneration system with supercritical and transcritical carbon dioxide power cycles, humidification-dehumidification system and hydrogen generation,” Energy Convers. Manag., vol. 332, p. 119762, May 2025, doi: 10.1016/j.enconman.2025.119762.

[156]	Arthur D. Little, “U N L O C K I N G FUSION ENERGY.” [Online]. Available: https://www.adlittle.com/sites/default/files/reports/ADL_Unlocking_fusion_energy_2025%20%281%29.pdf

[157]	F. M. A. Hadi, H. H. Aly, and T. Little, “Harmonics Forecasting of Wind and Solar Hybrid Model Based on Deep Machine Learning,” IEEE Access, vol. 11, pp. 100438–100457, 2023, doi: 10.1109/ACCESS.2023.3314742.

[158]	M. I. Saleem, S. Saha, U. Izhar, and L. Ang, “Stability assessment of inverter‐based renewable energy sources integrated to weak grids,” IET Energy Syst. Integr., vol. 6, no. 4, pp. 525–544, Dec. 2024, doi: 10.1049/esi2.12151.

[159]	N. Institute, “Beyond FERC Order 2023: Considerations on Deep Interconnection Reform”, [Online]. Available: https://www.researchgate.net/publication/382074664_Beyond_FERC_Order_2023_Considerations_on_Deep_Interconnection_Reform

[160]	S. Talebi and H. H. Aly, “Optimized Renewable Energy Integration: Advanced Modeling, Control, and Design of a Standalone Microgrid Using Hybrid FA-PSO,” IEEE Access, vol. 13, pp. 63486–63503, 2025, doi: 10.1109/ACCESS.2025.3559725.

[161]	H. Chen, Z. Zhang, C. Guan, and H. Gao, “Optimization of sizing and frequency control in battery/supercapacitor hybrid energy storage system for fuel cell ship,” Energy, vol. 197, p. 117285, Apr. 2020, doi: 10.1016/j.energy.2020.117285.

[162]	J. Lu, R. Xiong, J. Tian, C. Wang, and F. Sun, “Deep learning to estimate lithium-ion battery state of health without additional degradation experiments,” Nat. Commun., vol. 14, no. 1, p. 2760, May 2023, doi: 10.1038/s41467-023-38458-w.

[163]	S. Chatterjee, “Mitigating Supply Chain Malware Risks in Operational Technology: Challenges and Solutions for the Oil and Gas Industry”.

[164]	M. G. Todeschini, G. Dondossola, and R. Terruggia, “IMPACT EVALUATION OF IEC 62351 CYBER SECURITY ON IEC 61850 COMMUNICATIONS PERFORMANCE,” 2019.

[165]	A. Dimakopoulou and K. Rantos, “Comprehensive Analysis of Maritime Cybersecurity Landscape Based on the NIST CSF v2.0,” J. Mar. Sci. Eng., vol. 12, no. 6, p. 919, May 2024, doi: 10.3390/jmse12060919.